{"text_format":"1","workbook":"xlsx","n_sheets":8,"sheets":["Home Page","Tab 2   Inputs and Plots","Tab 3 Attenuation Factor","Tab 4 Mass Loading","Tab 5 Differential Pressure","Tab 6 Tracer Tests","Tab 7 H-J Model Assumptions","Calculations"],"not_rendered":{"charts":8,"images":7,"macros":1,"external_links":0,"defined_names":7,"comments":2,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Home Page","index":0,"n_rows":33,"n_cols":5,"rows_kept":33,"cut":false,"hidden":false,"merged":[[12,3,12,4],[1,1,1,2],[22,1,22,2],[23,1,23,2],[24,1,24,2],[12,1,12,2],[4,1,4,2],[3,1,3,2],[2,1,2,2],[13,2,14,2],[13,1,14,1],[1,3,1,4]]}
[]
[null,null,null,"2020-10-04"]
[null,"VIM Model V2.2"]
[null,"Vapor Intrusion Mitigation Model"]
[null,"Introduction: This spreadsheet tool was developed to help users: 1)  interpret the results of subslab venting pilot tests, 2) calculate building-specific attenuation factors from flow and vacuum data (McAlary et al., 2018), 3) assess the mass removal rate of a vapor mitigation system and 4) interpret high volume sampling (HVS) testing programs (McAlary et al, 2010).  Stepwise instructions for use of this spreadsheet are provided in the numbered list below.  The user should be familiar with the assumptions and limitations of the Hantush Jacob (1955) model (see Tab 7) and is referred to the Final Report for ESTCP ER201322 for a more complete description: https://www.serdp-estcp.org/Program-Areas/Environmental-Restoration/Contaminated-Groundwater/Emerging-Issues/ER-201322/ER-201322.  No warranty is expressed or implied."]
[null,"Glossary:"]
[null,null,"Transmissivity (T): the product of the gas condutivity (K) and thickness (b) of the zone of horizontal flow below the floor slab (i.e., T = K b)"]
[null,null,"Leakance (B): a term that accounts for the vertical gas conductivity of the floor (K'), thickness of the floor (b') and the Transmissivity (B = (Tb'/K')^0.5"]
[null,null,"Gas conductivity (K): Related to intrinsic permeability (k), but specific to the fluid's kinematic viscosity (v) (i.e., K = kg/v, where g = 9.8m/s^2)"]
[null,null,"Radius of Influence: radial distance within which the extraction of gas from below the floor is protective of indoor air quality."]
[null,null,"Target Level: performance metric considered protective (e.g., static vacuum > ambient fluctuations, velocity > 3 ft/day, travel time < 1day, etc.)"]
[null,null,"Granular Fill: Sand/gravel purposesfully placed below the floor slab to promote water drainage and typically compacted to provide structual support."]
[null,"Instructions:",null,"Location"]
[null,1,"Perform a test of gas extraction from a suction point and measure static vacuum at communication test points at various radial distances (see details in Tab 6).  Measure the flow rate (Q) and enter into cells N36 to N40 on Tab 2.  Enter static vacuum and radial distances in cells P44 to Q51 on Tab 2.  It is helpful to have static vacuum measurements at various radial distances to provide better calibration of the Transmissibity (T) and Leakance (B) values when fitting the curves on Figures 2.1a and 2.1b  on Tab 2 to the measured vacuum data.  One point at a short radial distance (e.g. ~3 ft or 1 m) helps calibrate the T value (which affects the y-intercept on Figure 2.1 and is most easily fitted using Figure 2.1a), and one or more points at longer radial distances (e.g., ~30 ft or 10 m or more) helps to calibrate the B value (which affects the slope of the curves on Figure 2.1a,b and is most easily fitted using Figure 2.1b).  Figures 2.1a and 2.1b are the same except the axes using linear and logarithmic scales are exchanged.  The wellhead vacuum is not recommended to be used as part of the curve-fitting on Figure 2.1a,b because it will often be biased high because of turbulence and frictional losses (this value is still useful for selecting an appropriate fan to overcome the frictional losses).","Tab 2","N-36-N40"]
[null,null,null,"Tab 2","P44 to Q51"]
[null,2,"Enter best estimates of thickness of zone of active flow (b) and effective porosity (n) in cells Q36 to R38 on Tab 2.  The thickness can be approximated as the thickness of a granular fill layer if the native soil has lower permeability by an order of magnitude or more.  The effective porosity can be estimated to be in the range of 20 to 30% in most cases.  In some cases, a gap exists below the floor slab as evidenced by a drop in the bit of a coring tool or hammer drill at the bottom of the slab, in which case, the thickness could be much smaller (e.g. 0.05 ft) and the porosity set to 1, as the \"fast\" option for the sensitivity analysis (Tab 2, cells M39 to R39).  For the \"fast\" option, use smaller values for b and n.  For the \"slow\" option (Tab 2, cells M40 to R40), use larger values for b and n. ","Tab 2","Q36 to R38"]
[null,3,"Adjust T and B values in cells O36 to P38 of Tab 2 until corresponsing lines provide an upper-range, lower-range and best fit through the measured vacuum data in the vacuum vs radial distance plot (Figure 2.1a and 2.1b on Tab 2).  T depends on the gas permeability and thickness of the dominant flow layer, which are often controlled during construction and therefore reasonably uniform, therefore a single T value is often adequate to fit the model to the data on both Figure 2.1a and 2.1b. A higher value for T results in a lower y-intercept on Figures 2.1a,b and vice-versa.  B depends on leakage, which occurs through discontinuities and is therefore generally not uniform, therefore a range of B values is often required to fit the model to the data.  A lower value for B results in a steeper slope on Figure 2.1b, and vice versa.  Adjust B and T values in rows 36 to 38 and columns O and P on Tab 2 to establish a best fit between the model and the static vacuum data.  The upper and lower estimates of the range are useful where the vacuum vs distance data does not all fit on one model curve.","Tab 2","O36 to P38"]
[null,4,"If tracer tests are conducted (as described on Tab 6 and in the Final Report for ESTCP ER201322), enter the travel time data in cells R44 to R51 on Tab 2.  Adjust the thickness and effective porosity values in cells Q39 to R40 of Tab 2 as needed to bracket the travel time vs radial distance data (Figure 2.2 on Tab 2).  Lower estimates for thickness and porosity result in fast velocities and short travel times and vice-versa.  See Tab 6 for example plots of Inter-Well and Flood tracer test data.  The model parameters (T, B, n, b) are established from the calibrations performed in these first four steps, and are used to generate the curves in Figures 2.3 and 2.4 of Tab 2 (i.e., no additional field measurments are required, so Figures 2.3 and 2.4 do not have measured data points).","Tab 2","R44 to R51"]
[null,5,"Adopt or adjust target levels for vacuum, velocity, travel time and proportion of flow per unit area in cells N44 to N54 of Tab 2.  If ambient cross-slab differential pressure data are available, use Tab 5 to evaluate the 95th percentile of the magnitude of the measured differential pressure, when averaged over an appropriate interval of time (e.g. averaged over at least one minute or more, and use judgement to select a target vacuum if the 95th percentile values are different for different averaging times).  Enter the reasonable maximum cross-slab differential pressure in cell S48 on Tab 2 and the target vacuum value in cells N44 and N45 on Tab 2 will automatically match.","Tab 2","N44 to N54 and S48"]
[null,6,"The radius of influence (ROI) based on flux calculations (McAlary et al., 2020) is calculated in cells S36 to S40 on Tab 2.  Figures 2.1, 2.2, 2.3 and 2.4 on Tab 2 also indicate the radius of influence based on vacuum, velocity, travel time and proportion of flow acress the floor, respectively as the radial distance at which the model curves cross the red line corresponding to the target value.  Consider a range of ROI values for each line of evidence using the various model curves resulting from the sensitivity analysis.  Use this ROI analysis to select an appropriate number and spacing of suction points for a full-scale mitigation system design.  In general, the ROI based on velocity and travel-time is more appropriate when T values are high (i.e., a sub-slab ventilation scenario), and the ROI based on vacuum is more appropriate when T is low (i.e., a sub-slab depressurization scenario).  Professional judgement is required where the ROI values from the five lines of evidence are dissimilar.","Tab 2","S36 to S40 and Figures 2.1, 2.2, 2.3 and 2.4"]
[null,7,"The user may wish to consider the effect of fan selection on the analysis.  The fan curve for the selected fan can be used to assign a new value for Q in cells N36 to N40, which will cause the model curves to adjust accordingly, resulting in new values for the ROI.  More details on fan curves is available at http://www.wpb-radon.com/radon_fan_performance.html.","Tab 2","N36 to N40"]
[null,8,"As with all mathematical models, professional judgement is required when selecting model inputs and interpreting model outputs.  The model assumes that there is a layer of material through which horizontal radial flow occurs in response to gas extraction from a suction point, with downward leakage across the slab being the only supply of air to the system.  Locations with measured vacuum much less than expected from the calibrated model indicate that there is a supply of air with limited resistance that contributes to dissipating the vacuum, which could either be preferential leakage across the floor slab (i.e., a floor drain or poorly unsealed expansion joint) or preferential supply of gas from a subsurface utility, gravel-filled trench, or similar feature (see for example the data in tab 2 that are pre-populated in this spreadsheet - a vacuum of only 5 Pa at a radial distance of 15 ft is low compared to the rest of the trend, indicating a supply of air to the subsurface in proximity to that probe).   Locations where the measured travel time from tracer testing is faster than expected indicate that there may be a thin plenum below the floor slab from differential settlement or dessication shrinkage of geologic materials below the floor.  In either case, field measurements that appear to be outliers compared to the majority of the data provide clues that local conditions differ from the model assumptions, and should not be overlooked or ignored. "]
[null,"Copyright: Geosyntec Consultants, Inc., 2020."]
[null,"Authors: Gordon Thrupp, John Gallinatti, Todd McAlary, Darius Mali, Paul Nicholson, William Wertz, Elham Shirazi"]
[null,"Relevant Literature:"]
[null,null,"ESTCP ER2013-22 Final Report: https://www.serdp-estcp.org/Program-Areas/Environmental-Restoration/Contaminated-Groundwater/Emerging-Issues/ER-201322/ER-201322"]
[null,null,"Hantush, M.S. and C.E. Jacob, 1955. Non-steady radial flow in an infinite leaky aquifer, Am. Geophys. Union Trans., vol. 36, pp. 95-100."]
[null,null,"Massmann, J. W. Applying groundwater flow models in vapor extraction system design. J. Environ. Eng. 1989, 115(1), 129-149."]
[null,null,"McAlary, T.A., Nicholson, P., Yik, L.K., Bertrand, D. and G. Thrupp, 2010. High Purge Volume Sampling - A New Paradigm for Sub-Slab Soil Gas Monitoring, Groundwater Monitoring and Remediation, V. 30, No. 2, pp 73–85, Spring 2010."]
[null,null,"McAlary ,T., Wertz, W., Mali, D. and P. Nicholson, 2020. Mathematical Analysis and Flux-Based Radius of Influence for Radon/VOC Vapor Intrusion Mitigation Systems, accepted on June 3 2020 for publication in the Science of the Total Environment, https://doi.org/10.1016/j.scitotenv.2020.139988 "]
[null,null,"McAlary, T., Gallinatti, J., Thrupp, G., Wertz, W., Mali, D. and H. Dawson, 2018.  Fluid Flow Model for Predicting the Intrusion Rate of Subsurface Contaminant Vapors into Buildings, Environmental Science & Technology, 2018, 52(15), pp 8438-8445."]
[null,null,"Thrupp, G., J. Gallinatti, and K. Johnson, 1996.  Tools to Improve Models for Design and Assessment of Soil Vapor Extraction Systems.  Subsurface Fluid-Flow Modeling, ASTM STP 1288, eds. J.D. Ritchey and J.O. Rumbaugh, American Society for Testing and Materials, Philadelphia, pp. 268-285."]
[null,null,"Thrupp, G., J. Baker, and J. Gallinatti. 1998. Leakage controls radius of influence of landfill gas extraction wells. In Proceedings of the 20th International Madison Waste Conference, University of Wisconsin, Madison, 363–372. "]

{"sheet":"Tab 2   Inputs and Plots","index":1,"n_rows":574,"n_cols":43,"rows_kept":574,"cut":false,"hidden":false,"merged":[[41,18,46,18],[41,15,41,17],[31,12,32,17],[4,0,5,5],[42,12,42,13],[45,12,45,13],[69,22,69,23],[69,24,69,25],[69,26,69,27],[69,30,69,31],[48,12,48,13],[51,12,51,13]]}
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,"SENSITIVITY ANALYSIS"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,"Legend Label","Flow rate, Q","Transmissivity, T","Leakance, B","Thickness, b","Effective Porosity, n","ROI based on Flux"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,"(ft3/min)","(ft2/d)","(ft)","(ft)","(v/v)","(ft)"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Upper bound",15,98,16,0.5,0.25,{"$f":"AF72","v":77.169874519291909}]
[null,null,null,null,null,null,null,null,null,null,null,null,"Lower Bound",15,32,4,0.5,0.25,{"$f":"AF73","v":22.658162606250116}]
[null,null,null,null,null,null,null,null,null,null,null,null,"Best Fit",15,86,14,0.5,0.25,68.894643612264474]
[null,null,null,null,null,null,null,null,null,null,null,null,"Best Fit (fast)",15,86,14,0.4,0.2,69.590549103297448]
[null,null,null,null,null,null,null,null,null,null,null,null,"Best Fit (slow)",15,86,14,0.6,0.3,68.894643612264474]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,"Radius (ft)","Target Levels","Monitoring Point","Field Measurments",null,null,"Reasonable Maximum Ambient Cross-Slab Pressure Differential (Pa)"]
[null,null,null,null,null,null,null,null,null,null,null,null,"Vacuum (Pascals)",null,"ID Number","radius (ft)","Vacuum (Pa)","Travel Time (min)"]
[null,null,null,null,null,null,null,null,null,null,null,null,0,{"$f":"S48","v":3},null,3,250]
[null,null,null,null,null,null,null,null,null,null,null,null,500,{"$f":"S48","v":3},null,5,180,0.7]
[null,null,null,null,null,null,null,null,null,null,null,null,"Velocity (ft/day)",null,null,10,90,3.3]
[null,null,null,null,null,null,null,null,null,null,null,null,0,3,null,15,5,7]
[null,null,null,null,null,null,null,null,null,null,null,null,500,{"$f":"N47","v":3},null,25,20,null,3]
[null,null,null,null,null,null,null,null,null,null,null,null,"Travel Time (minutes)",null,null,40,5]
[null,null,null,null,null,null,null,null,null,null,null,null,0,1440,null,50,3]
[null,null,null,null,null,null,null,null,null,null,null,null,500,{"$f":"N50","v":1440}]
[null,null,null,null,null,null,null,null,null,null,null,null,"Qsoil/Area (L/min/1000ft2)"]
[null,null,null,null,null,null,null,null,null,null,null,null,0,5]
[null,null,null,null,null,null,null,null,null,null,null,null,500,{"$f":"N53","v":5}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Constants","value","units"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"deltaP",{"$f":"S48*0.0832","v":0.24959999999999999},"m of air","differential pressure across the floor slab (positive for flow into building)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Deff",9.9999999999999995E-7,"m2/s","effective diffusion coefficient for vapor or gas of interest through material below the floor slab"]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"gas extraction flow rate",null,"Transmissivity",null,"Leakance",null,"flux balance","argument","ROI via flux balance"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Q (scfm)","Q (m3/s)","T (ft2/day)","T (m2/s)","B (ft)","B (m)","K1(r/B)","(r/B)","r (m)","r (ft)",null,null,null,null,null,null,null,null,null,"K1(r/B)","(r/B)"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"N36","v":15},{"$f":"W72*0.3048*0.3048*0.3048/60","v":7.0792116480000011E-3},{"$f":"O36","v":98},{"$f":"Y72*0.3048*0.3048/1440/60","v":1.0537613333333334E-4},{"$f":"P36","v":16},{"$f":"AA72*0.3048","v":4.8768000000000002},{"$f":"(2*3.14159*(Q36*0.3048)*AB72/X72)*((Z72*$Z$67/(AB72^2))+($Z$68/(Q36*0.3048)))","v":5.0579319095406692E-3},{"$f":"VLOOKUP(AC72,$AP$72:$AQ$574,2,TRUE)","v":4.8231171574557443},{"$f":"AB72*AD72","v":23.521377753480174},{"$f":"AE72/0.3048","v":77.169874519291909},null,null,null,null,null,null,null,null,null,{"$f":"BESSELK(AQ72,1)","v":7.3607848620602813E-67},150]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"N37","v":15},{"$f":"W73*0.3048*0.3048*0.3048/60","v":7.0792116480000011E-3},{"$f":"O37","v":32},{"$f":"Y73*0.3048*0.3048/1440/60","v":3.4408533333333334E-5},{"$f":"P37","v":4},{"$f":"AA73*0.3048","v":1.2192000000000001},{"$f":"(2*3.14159*(Q37*0.3048)*AB73/X73)*((Z73*$Z$67/(AB73^2))+($Z$68/(Q37*0.3048)))","v":2.0349352493667944E-3},{"$f":"VLOOKUP(AC73,$AP$72:$AQ$574,2,TRUE)","v":5.664540651562529},{"$f":"AB73*AD73","v":6.9062079623850359},{"$f":"AE73/0.3048","v":22.658162606250116},null,null,null,null,null,null,null,null,null,{"$f":"BESSELK(AQ73,1)","v":3.3155771961544897E-66},{"$f":"AQ72*0.99","v":148.5}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,15,7.0792116480000011E-3,86,9.247293333333334E-5,14,4.2671999999999999,4.5190060686967921E-3,{"$f":"VLOOKUP(AC74,$AP$72:$AQ$574,2,TRUE)","v":4.9210459723046061},20.999087373018213,68.894643612264474,null,null,null,null,null,null,null,null,null,1.47122757258952E-65,{"$f":"AQ73*0.99","v":147.01499999999999}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,15,7.0792116480000011E-3,86,9.247293333333334E-5,14,4.2671999999999999,4.3726786254605302E-3,{"$f":"VLOOKUP(AC75,$AP$72:$AQ$574,2,TRUE)","v":4.9707535073783902},21.211199366685065,69.590549103297448,null,null,null,null,null,null,null,null,null,6.4320795111572405E-65,145.54485]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,15,7.0792116480000011E-3,86,9.247293333333334E-5,14,4.2671999999999999,4.6653335119330548E-3,{"$f":"VLOOKUP(AC76,$AP$72:$AQ$574,2,TRUE)","v":4.9210459723046061},20.999087373018213,68.894643612264474,null,null,null,null,null,null,null,null,null,2.7710112208287405E-64,144.08940150000001]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.1765336271906786E-63,142.64850748500001]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.9239404863488034E-63,141.22202241015]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.0315439148400318E-62,139.8098021860485]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.2643091667042693E-62,138.41170416418802]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.3152413557613492E-61,137.02758712254615]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.3116341675899576E-60,135.65731125132069]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.1186964816687683E-60,134.30073813880747]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.9706733063844059E-59,132.9577307574194]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.4857859457300861E-59,131.6281534498452]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.8059893420479958E-58,130.31187191534676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.0380498645008078E-57,129.00875319619328]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.7904534538221823E-57,127.71866566423135]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.3663484474114759E-56,126.44147900758904]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.8627858494405506E-56,125.17706421751315]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.7089040008284738E-55,123.92529357533802]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.9308091462246079E-55,122.68604063958463]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.0329577619909127E-54,121.45918023318879]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.883585461703973E-54,120.24458843085689]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.3026413069952464E-53,119.04214254654832]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.6105466694201593E-53,117.85172112108283]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.4856250580487781E-52,116.673203909872]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.0230091381996819E-52,115.50647187077328]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.5595996516171333E-51,114.35140715206555]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.0721747839828013E-51,113.20789308054489]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.5167669129802797E-50,112.07581414973944]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.7585224748320634E-50,110.95505600824205]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.3650907205200035E-49,109.84550544815963]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.1301393213305827E-49,108.74705039367804]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.1260714061386373E-48,107.65957988974125]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.2709740399662687E-48,106.58298409084384]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.8298551580850118E-47,105.5171542499354]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.2828677529204619E-47,104.46198270743605]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.5091776545355501E-46,103.41736288036169]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.2665262621682709E-46,102.38318925155808]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.1937607041340675E-45,101.35935735904249]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.306083728499864E-45,100.34576378545206]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.0637641728397982E-45,99.34230614759754]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.4600591389135074E-44,98.34888308612156]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.6110170949903557E-44,97.365394255260341]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.7592191369546556E-43,96.391740312707739]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.6359980329713318E-43,95.427822909580655]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.2099863586617626E-42,94.473544680484849]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.1280486435654865E-42,93.528809233679993]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.0105762793650577E-42,92.593521141343189]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.0323209394876814E-41,91.667585929929757]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.1085742911719687E-41,90.750910070630454]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.2724075570706522E-40,89.843400969924147]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.1405931803266604E-40,88.944966960224903]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.6823742177626372E-40,88.05551729062266]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.8625870763041892E-39,87.174962117716433]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.4762434042117132E-39,86.303212496539274]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.0664120130188535E-38,85.440180371573874]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.518769644018154E-38,84.585778567858128]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.8984980822988456E-38,83.739920782179553]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.3696863027174123E-37,82.902521574357763]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.1540182217755683E-37,82.073496358614179]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.2028947413871483E-37,81.252761395028031]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6314949337063486E-36,80.440233781077751]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.6655219765660632E-36,79.635831443266966]
[null,null,null,{"$f":"0.5*75*28","v":1050},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.1694468636086193E-36,78.8394731288343]
[null,null,null,{"$f":"25*28","v":700},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"BESSELK(AQ137,1)","v":1.8063052338414866E-35},78.05107839754595]
[null,null,null,{"$f":"SUM(D136:D137)","v":1750},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.9624690127000209E-35,{"$f":"AQ137*0.99","v":77.270567613570492}]
[null,null,null,{"$f":"1-(D138/2800)","v":0.375},null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.6248412449551852E-35,76.497861937434791]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.862862208049525E-34,75.732883318060445]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.9928988290947049E-34,74.975554484879837]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.4938982999534381E-34,74.225798940031041]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.7933698990479134E-33,73.483540950630726]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.758454766057526E-33,72.748705541124423]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.8191158887722407E-33,72.021218485713177]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6149041783879142E-32,71.301006300856045]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.3113741116975303E-32,70.587996237847477]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.7417617904443777E-32,69.882116275469002]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.3629288626730034E-31,69.183295112714305]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.7361396735487567E-31,68.491462161587165]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.4550530577222481E-31,67.806547539971291]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.0801532681624055E-30,67.128482064571571]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.1243556493762332E-30,66.457197243925862]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.1500559837886562E-30,65.7926252714866]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.053686644747823E-30,65.134699018771727]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.5526673055162156E-29,64.483352028584008]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.9739493782087494E-29,63.838518508298165]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.6596361107468648E-29,63.200133323215184]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.0702154755197654E-28,62.56813198998303]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.0109878759872206E-28,61.942450670083197]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.7551789323690884E-28,61.323026163382366]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.9688634118457228E-28,60.709795901748542]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.2853763544690495E-27,60.102697942731055]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.3564722635035422E-27,59.501670963303745]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.2942210716690427E-27,58.906654253670709]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.7789792025228881E-27,58.317587711134003]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.400886052313731E-26,57.734411834022666]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.5081331426236675E-26,57.157067715682437]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.4646895634350253E-26,56.58549703852561]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.9022347699003244E-26,56.01964206814035]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.3907574522263655E-25,55.459445647458942]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.4339981707738772E-25,54.904851190984353]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.2362425222898481E-25,54.355802679074507]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.3325863746937625E-25,53.812244652283759]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.262330896283779E-24,53.274122205760918]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.1614863534025863E-24,52.741380983703309]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.6814458657285187E-24,52.213967173866273]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.2372638184706024E-24,51.691827502127609]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.0512414862965902E-23,51.174909227106333]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.7626505918510466E-23,50.663160134835266]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.9404092818818581E-23,50.156528533486913]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.8803321562794435E-23,49.654963248152043]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.0595914123206169E-23,49.158413615670526]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.3244040605975561E-22,48.666829479513822]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.1656755012505652E-22,48.180161184718685]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.5241389059696983E-22,47.698359572871496]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.7071665369024E-22,47.221375977142777]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.198497483857326E-22,46.749162217371349]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.4755800719570569E-21,46.281670595197639]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.356018624182804E-21,45.818853889245659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.7444239434656853E-21,45.360665350353202]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.9238188300255439E-21,44.907058696849667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.3292962485855057E-21,44.457988109881171]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.4626690294864834E-20,44.01340822878236]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.2830363114384407E-20,43.573274146494533]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.5478761834698304E-20,43.137541405029587]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.4894911896803305E-20,42.706165990979294]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.4571232155032023E-20,42.279104331069497]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.2973551794606848E-19,41.856313287758802]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.9817977859221902E-19,41.437750154881215]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"BESSELK(AQ201,1)","v":3.0146879835308439E-19},41.023372653332402]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.5669490293265546E-19,{"$f":"AQ201*0.99","v":40.613138926799074}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.89015073276058E-19,40.207007537531084]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.0353039350717408E-18,39.80493746215577]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.5493917240945911E-18,39.406888087534213]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.3095442622815974E-18,39.012819206658868]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.4291014157179108E-18,38.622691014592277]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.0715471677700876E-18,38.236464104446355]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.4717727582929923E-18,37.854099463401894]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.0965960201391714E-17,37.475558468767872]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6033417805109695E-17,37.100802884080196]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.3354922580238353E-17,36.72979485523939]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.3893772614711555E-17,36.362496906686999]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.9007964537607593E-17,35.99887193762013]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.0604868514084332E-17,35.638883218243926]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.0135371173173992E-16,35.282494386061487]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.4497640668275494E-16,34.929669442200868]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.0664416705839067E-16,34.58037274777886]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.9351644858940901E-16,34.234569020301073]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.1547068358782538E-16,33.892223330098062]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.8608687386785858E-16,33.553301096797078]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.2397141862863463E-16,33.217768085829107]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.1545309126543316E-15,32.885590404970813]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.612340734046276E-15,32.556734500921102]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.244297157962259E-15,32.231167155911891]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.1137981223541986E-15,31.90885548435277]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.3062699242437156E-15,31.589766929509242]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.9364491294643357E-15,31.273869260214148]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.1579458970155521E-15,30.961130567612006]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.1175762995496171E-14,30.651519261935885]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.526263169873104E-14,30.345004069316527]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.0780260891309076E-14,30.041554028623363]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.8206890565677336E-14,29.741138488337128]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.8172909404791834E-14,29.443727103453757]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.150675523029442E-14,29.149289832419218]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.929388718222138E-14,28.857796934095024]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.295232416851905E-14,28.569218964754075]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.2432911487293599E-13,28.283526775106534]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6582317569412175E-13,28.000691507355469]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.20541246411141E-13,27.720684592281913]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.9249531900659087E-13,27.443477746359093]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.8685185195170768E-13,27.169042968895504]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.1024545998478486E-13,26.897352539206548]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.7117264983297149E-13,26.628379013814481]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.8048465132481372E-13,26.362095223676334]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.1520025828934807E-12,26.098474271439571]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.5032832209157663E-12,25.837489528725175]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.9565696648806256E-12,25.579114633437925]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.5399683798881483E-12,25.323323487103547]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.2889026559815734E-12,25.070090252232511]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.2479026818443945E-12,24.819389349710185]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.4728044535818278E-12,24.571195456213083]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.0334439302665303E-12,24.32548350165095]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.0169495509432686E-12,24.082228666634439]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.1531755833264812E-11,23.841406379968095]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.4712483723150985E-11,23.602992316168415]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.8725860154976748E-11,23.36696239300673]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.377788047107948E-11,23.133292769076665]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.0122453562686519E-11,22.901959841385899]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.8071811528787048E-11,22.672940242972039]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.8009014080101867E-11,22.446210840542317]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.0402933701110713E-11,22.221748732136895]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.5826171672822537E-11,21.999531244815525]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.4976428496985089E-11,21.77953593236737]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"BESSELK(AQ265,1)","v":1.1870193619445997E-10},21.561740573043696]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.4803165562911998E-10,{"$f":"AQ265*0.99","v":21.346123167313259}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.8421105079855905E-10,21.132661935640126]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.2874437541569329E-10,20.921335316283724]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.8344454668366781E-10,20.712121963120886]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.5049183866781371E-10,20.505000743489678]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.3250280494765936E-10,20.299950736054782]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.3261103927357543E-10,20.096951228694234]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.5456160587105239E-10,19.895981716407292]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.0282122007519794E-10,19.697021899243218]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.8270653751093506E-10,19.500051680250785]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.2005332185574229E-9,19.305051163448276]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.4637887769645837E-9,19.112000651813794]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.7813325999541658E-9,18.920880645295657]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.1636269447701044E-9,18.731671838842701]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.6230031763683841E-9,18.544355120454274]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.1739680157600412E-9,18.358911569249731]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.8335551215111944E-9,18.175322453557232]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.6217279311760213E-9,17.993569229021659]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.5618403481328598E-9,17.813633536731441]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.6811625755527069E-9,17.635497201364128]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.0114801761740788E-9,17.459142229350487]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.5897752772555851E-9,17.284550807056981]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.1458999747516648E-8,17.111705298986411]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.3668951149927556E-8,16.940588245996548]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6277263323594527E-8,16.771182363536582]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.9350524572238303E-8,16.603470539901217]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.2965537638190181E-8,16.437435834502203]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.7210736921464498E-8,16.273061476157181]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.2187779765038407E-8,16.11033086139561]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.8013330071341691E-8,15.949227552781654]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.4821054042104749E-8,15.789735277253838]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.2763849444647328E-8,15.631837924481299]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.2016331502441403E-8,15.475519545236486]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.2777600285842329E-8,15.32076434978412]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.5274316339152781E-8,15.167556706286279]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.9764113220947464E-8,15.015881139223415]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.1653937765345503E-7,14.865722327831181]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.3593143007066727E-7,14.717065104552869]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.5831514051988987E-7,14.56989445350734]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.8411401710303673E-7,14.424195508972266]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.1380580643669425E-7,14.279953553882544]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.4792864795756486E-7,14.137154018343718]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.8708782629524902E-7,13.995782478160281]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.3196316836947733E-7,13.855824653378678]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.8331713433497596E-7,13.717266406844891]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.4200365398447307E-7,13.580093742776441]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.0897776271827359E-7,13.444292805348676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.8530609368594688E-7,13.309849877295189]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.7217828518965491E-7,13.176751378522237]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.7091936489639373E-7,13.044983864737015]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.8300317482406727E-7,12.914534026089644]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.0100669034291948E-6,12.785388685828748]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.1539267934169092E-6,12.65753479897046]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.3165950961007324E-6,12.530959450980754]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.5002983452440252E-6,12.405649856470946]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.7074970252998925E-6,12.281593357906237]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.9409067108144098E-6,12.158777424327175]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.2035207554515352E-6,12.037189650083903]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.4986346106191613E-6,11.916817753583064]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.8298718550063005E-6,11.797649576047233]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.2012120174633692E-6,11.67967308028676]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.6170202765531436E-6,11.562876349483892]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.0820791207511428E-6,11.447247585989052]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"BESSELK(AQ329,1)","v":4.6016220536639345E-6},11.332775110129161]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.1813694287450185E-6,{"$f":"AQ329*0.99","v":11.219447359027869}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.8275664978041373E-6,11.107252885437591]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.5470237571115998E-6,10.996180356583215]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.3471596740797208E-6,10.886218553017383]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.2360458763444735E-6,10.777356367487208]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.2224548835600702E-6,10.669582803812336]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.0315910460344764E-5,10.562886975774212]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.1526740666568274E-5,10.45725810601647]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.2866133678540775E-5,10.352685524956305]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.4346196451643072E-5,10.249158669706743]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.5980016291521452E-5,10.146667083009675]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.7781725397155288E-5,10.045200412179577]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.9766568434888637E-5,9.9447484080577819]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.19509731978976E-5,9.845300923977204]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.4352624400545567E-5,9.7468479147374314]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.6990540651662793E-5,9.6493794355900562]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.9885154644978724E-5,9.5528856412341554]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.3058396598744908E-5,9.4573567848218136]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.6533780970021112E-5,9.3627832169735949]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.0336496462171091E-5,9.2691553848038595]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.4493499336839146E-5,9.1764638309558215]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.9033610034070923E-5,9.0846991926462639]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.3987613096320813E-5,8.9938522007198021]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.9388360383871204E-5,8.9039136787126036]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.5270877560698917E-5,8.8148745419254784]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.167247382108652E-5,8.7267257965062228]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.8632854818309618E-5,8.6394585385411613]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.6194238747574358E-5,8.5530639531557497]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.4401475526044315E-5,8.4675333136241928]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.0330216900333105E-4,8.3828579804879499]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.1294680212623967E-4,8.2990294006830698]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.2338886497191196E-4,8.2160391066762397]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.3468498555380755E-4,8.1338787156094767]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.468950632952593E-4,8.0525399284533812]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6008240505565989E-4,7.9720145291688471]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.7431386358471613E-4,7.8922943838771582]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.8965997827068295E-4,7.8133714400383862]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.0619511803910182E-4,7.7352377256380027]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.2399762624934579E-4,7.6578853483816225]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.4314996742725057E-4,7.5813064948978059]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.6373887566334074E-4,7.5054934299488281]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.8585550449764901E-4,7.4304384956493399]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.0959557810393128E-4,7.3561341106928468]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.3505954357822997E-4,7.2825727695859186]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.6235272412925415E-4,7.2097470418900595]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.9158547296097346E-4,7.137649571471159]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.2287332763118205E-4,7.0662730757564471]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.5633716466361653E-4,6.9956103449988829]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.921033541855287E-4,6.9256542415488944]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.3030391435744456E-4,6.8563976991334057]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.7107666535721627E-4,6.7878337221420715]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.1456538267641082E-4,6.7199553849206506]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.6091994948359195E-4,6.6527558310714436]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.1029650780616801E-4,6.5862282727607289]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.6285760828020911E-4,6.5203659900331212]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.187723582159898E-4,6.4551623301327901]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.7821656772601141E-4,6.3906107068314624]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.4137289366189535E-4,6.3267045997631479]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.0084309811068321E-3,6.2634375537655167]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.0795876021712229E-3,6.2008031782278614]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.1550467918407495E-3,6.1387951464455828]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.2350199806283814E-3,6.0774071949811272]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.3197261237847383E-3,6.0166331230313155]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"BESSELK(AQ393,1)","v":1.4093918268247819E-3},5.9564667918010024]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.5042514671330383E-3,{"$f":"AQ393*0.99","v":5.8969021238829926}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6045473114143481E-3,5.837933102644163]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.7105296287626226E-3,5.7795537716177217]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.8224567991261082E-3,5.7217582339015447]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.9405954169543114E-3,5.664540651562529]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.065220389818931E-3,5.6078952450469037]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.1966150318088996E-3,5.5518162925964347]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.3350711515078885E-3,5.4962981296704703]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.4808891343714242E-3,5.4413351483737653]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.634378019330003E-3,5.3869217968900278]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.7958555694542735E-3,5.3330525789211274]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.9656483365284739E-3,5.2797220531319162]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.1440917193888509E-3,5.2269248326005968]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.3315300158945605E-3,5.1746555842745909]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.5283164684098726E-3,5.1229090284318453]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.7348133026878587E-3,5.0716799381475264]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.9513917600575805E-3,5.0209631387660512]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.1784321228287716E-3,4.9707535073783902]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.4163237328401269E-3,4.9210459723046061]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.6654650030897391E-3,4.8718355125815602]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.9262634223986379E-3,4.8231171574557443]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.1991355530709455E-3,4.7748859858811867]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.4845070215268649E-3,4.7271371260223747]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.7828125018972729E-3,4.6798657547621509]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.0944956925814385E-3,4.6330670972145294]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.4200092857818773E-3,4.5867364262423838]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.7598149300430411E-3,4.5408690619799597]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.1143831858328458E-3,4.49546037136016]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.4841934742184276E-3,4.4505057676465585]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.869734018699592E-3,4.4060007099700931]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.2715017802754403E-3,4.3619407028703918]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.6900023858313222E-3,4.3183212958416881]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.1257500499447933E-3,4.275138082883271]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.5792674902203737E-3,4.2323867020544386]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.0051085836273982E-2,4.1900628350338938]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.054174453249827E-2,4.1481622066835548]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.1051791234750606E-2,4.1066805846167194]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.1581781701115056E-2,4.065613778770552]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.2132279676899456E-2,4.024957640982846]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.2703856774037594E-2,3.9847080645730175]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.3297092345075394E-2,3.9448609839272875]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.3912573351927998E-2,3.9054123740880144]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.4550894229602701E-2,3.8663582503471341]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.5212656745089955E-2,3.8276946678436627]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.5898469851631535E-2,3.789417721165226]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.6608949538581386E-2,3.7515235439535739]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.7344718677080737E-2,3.7140083085140381]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.8106406861774279E-2,3.6768682254288976]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.8894650248799466E-2,3.6400995431746086]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,1.9710091390285251E-2,3.6036985477428627]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.0553379065600667E-2,3.567661562265434]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.1425168109597041E-2,3.5319849466427797]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.2326119238090834E-2,3.496665097176352]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.3256898870836346E-2,3.4616984462045886]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.42181789522397E-2,3.4270814617425427]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.5210636770067067E-2,3.3928106471251174]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.6234954772400954E-2,3.358882540653866]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.7291820383099318E-2,3.3252937152473274]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.8381925816012028E-2,3.292040778094854]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,2.9505967888209039E-2,3.2591203703139056]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.0664647832473933E-2,3.2265291666107663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.1858671109315111E-2,3.1942638749446588]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.3088747218745503E-2,3.1623212361952122]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"BESSELK(AQ457,1)","v":3.4355589512079281E-2},3.13069802383326]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.5659915003992078E-2,{"$f":"AQ457*0.99","v":3.0993910435949275}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.7002444185088017E-2,3.0683971331589781]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.8383900835213779E-2,3.0377131618273885]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,3.9805011837756511E-2,3.0073360302091148]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.1266506995158186E-2,2.9772626699070237]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.2769118845875087E-2,2.9474900432079534]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.431358248300634E-2,2.9180151427758738]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.5900635374810705E-2,2.8888349913481148]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.7531017187325393E-2,2.8599466414346337]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,4.9205469609295796E-2,2.8313471750202872]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.0924736179618658E-2,2.8030337032700845]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.2689562117495835E-2,2.7750033662373834]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.4500694155489221E-2,2.7472533325750095]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.6358880375661384E-2,2.7197807992492593]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,5.82648700489794E-2,2.6925829912567667]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.0219413478152989E-2,2.6656571613441988]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.2223261844070649E-2,2.6390005897307569]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.4277167055990722E-2,2.6126105838334492]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.6381881605636475E-2,2.5864844779951146]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,6.8538158425337004E-2,2.5606196332151634]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.0746750750348295E-2,2.5350134368830117]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.3008411985480359E-2,2.5096633025141815]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.5323895576148561E-2,2.4845666694890398]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,7.769395488395972E-2,2.4597210027941494]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.011934306693394E-2,2.4351237927662077]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.2600812964455844E-2,2.4107725548385455]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.513911698703977E-2,2.3866648292901598]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,8.7735007010984467E-2,2.3627981809972582]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.038923427798437E-2,2.3391701991872855]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.3102549299754436E-2,2.3157784971954127]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.5875701767717758E-2,2.2926207122234588]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,9.8709440467793438E-2,2.2696945051012243]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.10160451320031434,2.2469975600502119]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.10456166670509286,2.2245275844497097]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.10758164659164328,2.2022823086052123]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.11066519727455786,2.1802594855191604]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.11381306191402372,2.158456890663969]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.11702598236145456,2.1368723217573291]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.12030469911020063,2.1155035985397559]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.12364995125128764,2.0943485625543583]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.12706247643412175,2.0734050769288146]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.13054301083208428,2.0526710261595262]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.13409228911292589,2.0321443158979311]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.13771104441385479,2.0118228727389518]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.1414000086140737,1.9917046440115622]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.14515991702120518,1.9717875975714465]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.14899149506379405,1.9520697215957321]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.15289547007157722,1.9325490243797747]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.15687256788340437,1.9132235341359769]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.16092351286048134,1.894091298794617]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.16504902790504122,1.8751503858066709]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.16924983448436892,1.8563988819486041]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.17352665266010803,1.8378348931291182]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.17788020112277764,1.819456544197827]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.1823111972314265,1.8012619787558486]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.18682035705835143,1.7832493589682901]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.19140839543880495,1.7654168653786071]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.1960760260256168,1.747762696724821]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.20082396134865232,1.7302850697575727]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.20565291287902931,1.712982219059997]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.21056359109801237,1.695852396869397]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.21555670557050555,1.678893872900703]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.22063296502305701,1.662104934171696]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"BESSELK(AQ521,1)","v":0.22579307742629576},1.6454838848299791]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.23103775008171029,{"$f":"AQ521*0.99","v":1.6290290459816792}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.2363676897126871,1.6127387555218624]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.24178360255971632,1.5966113679666438]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.24728619447968092,1.5806452542869773]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.25287617104913462,1.5648388017441075]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.25855423767148178,1.5491904137266663]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.26432109968796552,1.5336985095893996]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.27017746249237512,1.5183615244935056]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.2761240316493771,1.5031779092485704]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.28216151301638009,1.4881461301560848]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.28829061286884167,1.4732646688545239]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.29451203802892056,1.4585320221659785]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.30082649599738559,1.4439467019443188]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.30723469508868784,1.4295072349248756]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.31373734456910335,1.4152121625756269]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.32033515479785418,1.4010600409498706]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.32702883737111943,1.3870494405403719]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.33381910526884123,1.3731789461349682]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.34070667300424085,1.3594471566736184]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.34769225677595106,1.3458526851068822]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.35477657462267986,1.3323941582558134]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.3619603465803175,1.3190702166732553]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.36924429484139937,1.3058795145065227]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.37662914391684182,1.2928207193614576]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.38411562079986394,1.2798925121678431]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.39170445513201685,1.2670935870461646]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.39939637937123523,1.2544226511757028]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.40719212896183327,1.2418784246639458]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4150924425063664,1.2294596404173064]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.42309806193928073,1.2171650440131334]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.43120973270227714,1.2049933935730022]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.43942820392131149,1.1929434596372721]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.44775422858516506,1.1810140250408994]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.45618856372550887,1.1692038847904904]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.46473197059839672,1.1575118459425855]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.47338521486711727,1.1459367274831596]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.4821490667863414,1.134477360208328]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.49102430138750197,1.1231325866062447]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.50001169866534023,1.1119012607401824]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.50911204376556407,1.1007822481327805]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.51832612717355553,1.0897744256514525]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.52765474490407416,1.078876681394938]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.53709869869190063,1.0680879145809885]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.54665879618336721,1.0574070354351786]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.55633585112872685,1.0468329650808268]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.56613068357530816,1.0363646354300184]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.57604412006141459,1.0260009890757182]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.58607699381091671,1.015740979184961]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.59623014492849891,1.0055835693931114]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.60650442059551857,0.99552773369918035]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.61690067526643566,0.98557245636218849]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.62741977086577738,0.97571673179856655]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,0.63806257698560231,0.96595956448058085]

{"sheet":"Tab 3 Attenuation Factor","index":2,"n_rows":22,"n_cols":7,"rows_kept":22,"cut":false,"hidden":false,"merged":[[0,0,1,6],[21,0,21,6],[2,0,2,6],[3,0,3,6],[4,0,4,6],[5,0,5,6]]}
["Building-Specific Attenuation Factor"]
[]
["Instructions"]
["1. Replace values in the grey shaded cells with site-specific data"]
["2. Cells will populate automatically based on Tab 2"]
["3. Range of site specifc attenuation factors "]
["Column1","Differential Pressure (ΔP)","Transmissivity (T)","Leakance (B)","Building Height (h)","Air Exchange Rate (AER)","Attenuation Factor (AF)"]
[null,"(ft of air head)","(ft2/d)","(ft)","(ft)","(day-1)","dimensionless"]
["Upper Estimate",{"$f":"'Tab 2   Inputs and Plots'!Z67/0.3048","v":0.81889763779527547},{"$f":"'Tab 2   Inputs and Plots'!O36","v":98},{"$f":"'Tab 2   Inputs and Plots'!P37","v":4},6,6,{"$f":"(B9*C9)/(D9^2*E9*F9)","v":0.13932633420822393}]
["Lower Estimate",0.01,{"$f":"'Tab 2   Inputs and Plots'!O37","v":32},{"$f":"'Tab 2   Inputs and Plots'!P36","v":16},10,24,{"$f":"(B10*C10)/(D10^2*E10*F10)","v":5.2083333333333332E-6}]
["Best Estimate",0.03,{"$f":"'Tab 2   Inputs and Plots'!O38","v":86},{"$f":"'Tab 2   Inputs and Plots'!P38","v":14},8,12,{"$f":"(B11*C11)/(D11^2*E11*F11)","v":1.371173469387755E-4}]
[]
[]
["Notes:","For Best Estimate, use values for all 5 inputs parameters that are mid-range values"]
[null,"For lower estimate of AF, use lower estimates of T and ΔP, and upper estimates of B, h and AER"]
[null,"For upper estimate of AF, use upper estimates of T and ΔP, and lower estimates of B, h and AER"]
[null,"Transmissivity and Leakance values are drawn from the flow and vacuum analysis on Tab 2"]
[null,"1 pascal of differential pressure = 0.27 feet of air column = 0.004 inches of water column = 0.0075 millimeters of mercury"]
[null,"1 foot of air column differential pressure = 3.7 pascals = 0.015 inches of water column = 0.027 mm Hg"]
[]
["Reference:"]
["McAlary, T., Gallinatti, J., Thrupp, G., Wertz, W., Mali, D. and H. Dawson, 2018.  Fluid Flow Model for Predicting the Intrusion Rate of Subsurface Contaminant Vapors into Buildings, Environmental Science & Technology, 2018, 52(15), pp 8438-8445."]

{"sheet":"Tab 4 Mass Loading","index":3,"n_rows":38,"n_cols":7,"rows_kept":38,"cut":false,"hidden":false,"merged":[[0,0,1,6],[39,0,39,6],[4,0,4,6],[3,0,3,6],[5,0,5,6],[2,0,2,6]]}
["Mass Loading Calculations"]
[]
["Instructions"]
["1. Replace values in the blue shaded cells with site-specific data"]
["2. Replace values in the green shaded cells with compound-specific indoor air screening level"]
["3. If Mass Removal Rate > Mass Loading Screening Level, the system operation is justified"]
[]
["SSV SYSTEM OPERATIONS","Extraction Flow Rate (Q)","Extraction Flow Rate (Q)2","Concentration of Target Compound","Mass Removal Rate"]
[null,"(ft3/min)","(m3/day)","(µg/m3) or (Bq/m3)","(g/day) or (MBq/day)"]
["Suction Point 1",50,{"$f":"B10*0.0283*1440","v":2037.6000000000001},100,{"$f":"D10*C10/1000000","v":0.20376}]
["Suction Point 2",70,{"$f":"B11*0.0283*1440","v":2852.64},200,{"$f":"D11*C11/1000000","v":0.57052800000000004}]
["Suction Point 3",30,1222.56,400,0.48902400000000001]
["Suction Point 4",40,1630.08,300,0.48902400000000001]
["Suction Point 5",50,2037.6000000000001,1200,2.4451200000000002]
["Suction Point 6",60,2445.12,200,0.48902400000000001]
["Suction Point 7",40,1630.08,400,0.65203199999999994]
["Suction Point 8",70,2852.64,300,0.855792]
["Suction Point 9",30,1222.56,200,0.24451200000000001]
["Suction Point 10",60,2445.12,500,1.2225600000000001]
["Suction Point 11",50,2037.6000000000001,700,1.42632]
["Suction Point 12",25,1018.8000000000001,1100,{"$f":"D21*C21/1000000","v":1.1206799999999999}]
[null,"Total Mass Removal Rate (g/day) or (MBq/day) = ",null,null,{"$f":"SUM(E10:E21)","v":10.208376000000001}]
[]
["SCREENING LEVEL CALCULATION","Floor Area (A)","Height","Volume","Air Exchange Rate (AER) (exchanges per day)","Indoor Air Screening Level","Mass Loading Screening Level (MLSL)"]
[null,"(ft2)","(ft)","(m3)","(day-1)","(µg/m3)  or (Bq/m3)","(g/day)  or (MBq/day)"]
["Air Zone 1",1000,10,{"$f":"C26*B26*0.3048*0.3048*0.3048","v":283.16846592000002},12,2.1,{"$f":"F26*E26*D26/1000000","v":7.1358453411840012E-3}]
["Air Zone 2",1500,10,{"$f":"C27*B27*0.3048*0.3048*0.3048","v":424.75269888000008},12,2.1,{"$f":"F27*E27*D27/1000000","v":1.0703768011776003E-2}]
["Air Zone 3",1200,10,339.80215910400005,12,2.1,8.5630144094208018E-3]
["Air Zone 4",2000,15,849.50539776000016,12,2.1,2.1407536023552005E-2]
["Air Zone 5",300,10,84.950539776000014,12,2.1,2.1407536023552005E-3]
["Air Zone 6",3000,15,1274.2580966400001,12,2.1,3.2111304035328005E-2]
["Air Zone 7",2100,10,594.65377843200008,12,2.1,1.4985275216486403E-2]
["Air Zone 8",1400,10,396.43585228800004,12,2.1,9.9901834776576024E-3]
["Air Zone 9",1800,10,509.70323865600011,12,2.1,1.2844521614131205E-2]
["Air Zone 10",1000,10,283.16846592000002,12,2.1,7.1358453411840012E-3]
["Air Zone 11",1100,10,311.48531251200006,12,2.1,7.8494298753024015E-3]
["Air Zone 12",1800,10,509.70323865600011,12,2.1,1.2844521614131205E-2]
[null,null,null,"Total Building MLSL (g/day)  or (MBq/day) = ",null,null,{"$f":"SUM(G26:G37)","v":0.14771199856250886}]

{"sheet":"Tab 5 Differential Pressure","index":4,"n_rows":12385,"n_cols":11,"rows_kept":4500,"cut":true,"hidden":false,"merged":[[8,6,8,9],[1,0,1,13]],"bounds":{"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0}}
["CROSS-SLAB DIFFERENTIAL PRESSURE ANALYSIS AND INTERPRETATION"]
["Instructions"]
["1. Use this tab to calculate a building-specific target value for the cross-slab differential pressure based on ambient cross-slab monitoring data"]
["2. Collect the ambient cross-slab differential pressure using a digital micromanometer with data-logging capabilities, at a 10 second interval and enter data as shown in columns A to I"]
["3. Column J calculates a 1-minute rolling average (as long as column J measurements are every 10 seconds), and Column K calculates 5-minute rolling average"]
["4. Order Statistics are calculated in Columns M to P.  The 95th percentile values are highlighted in yellow.  Enter this value in cell S48 of Tab 2."]
["5. Charts are provided for visualization"]
[]
[null,null,null,null,null,null,"CALCULATED ORDER STATISTICS"]
[]
[null,null,null,null,null,null,"Order statistics","10 second Average","1-Min Moving Average","5-Min Moving Average"]
[]
[null,null,null,null,null,null,"Average",{"$f":"AVERAGE(G$56:G$12385)","v":-0.34007542579075245},{"$f":"AVERAGE(J$61:J$12385)","v":-0.34016308316429983},{"$f":"AVERAGE(K$81:K$124385)","v":-0.34022586190729281}]
[null,null,null,null,null,null,"Min",{"$f":"MIN(G$56:G$12385)","v":-1.7999999999999998},{"$f":"MIN(J$61:J$12385)","v":-1.1349999999999998},{"$f":"MIN(K$81:K$12385)","v":-0.99923076923076937}]
[null,null,null,null,null,null,"5th%",{"$f":"PERCENTILE(G$56:G$12385,0.05)","v":-0.72},{"$f":"PERCENTILE(J$61:J$12385,0.05)","v":-0.69499999999999995},{"$f":"PERCENTILE(K$81:K$12385,0.05)","v":-0.63}]
[null,null,null,null,null,null,"25th%",{"$f":"PERCENTILE(G$56:G$12385,0.25)","v":-0.48},{"$f":"PERCENTILE(J$61:J$12385,0.25)","v":-0.47000000000000003},{"$f":"PERCENTILE(K$81:K$12385,0.25)","v":-0.45346153846153847}]
[null,null,null,null,null,null,"50th%",{"$f":"PERCENTILE(G$56:G$12385,0.5)","v":-0.33},{"$f":"PERCENTILE(J$61:J$12385,0.5)","v":-0.32500000000000001},{"$f":"PERCENTILE(K$81:K$12385,0.5)","v":-0.32769230769230767}]
[null,null,null,null,null,null,"75th%",{"$f":"PERCENTILE(G$56:G$12385,0.75)","v":-0.18},{"$f":"PERCENTILE(J$61:J$12385,0.75)","v":-0.19999999999999998},{"$f":"PERCENTILE(K$81:K$12385,0.75)","v":-0.22038461538461543}]
[null,null,null,null,null,null,"95th%",{"$f":"PERCENTILE(G$56:G$12385,0.95)","v":0},{"$f":"PERCENTILE(J$61:J$12385,0.95)","v":-0.03},{"$f":"PERCENTILE(K$81:K$12385,0.95)","v":-8.192307692307696E-2},"Enter this value in cell S48 of Tab 2"]
[null,null,null,null,null,null,"Max",{"$f":"MAX(G$56:G$12385)","v":0.66},{"$f":"MAX(J$61:J$12385)","v":0.32500000000000001},{"$f":"MAX(K$81:K$12385)","v":0.23653846153846153}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["Raw data entered in this row, delete left over data on end of dataset"]
["Month","Day","Year","Hour","Minute","Sec","Ch A","Ch B","Date and Time","Calculated 1-minute Moving Average (Pa)","Calculated 5-minute Moving Average (Pa)"]
[6,28,2018,8,34,49,0.06,0.06,{"$f":"DATE(C56,A56,B56)+TIME(D56,E56,F56)","v":"2018-06-28T08:34:49"}]
[6,28,2018,8,34,59,0.06,0.06,{"$f":"DATE(C57,A57,B57)+TIME(D57,E57,F57)","v":"2018-06-28T08:34:59"}]
[6,28,2018,8,35,9,0.06,0.06,"2018-06-28T08:35:09"]
[6,28,2018,8,35,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T08:35:19"]
[6,28,2018,8,35,29,0.06,0.06,"2018-06-28T08:35:29"]
[6,28,2018,8,35,39,0.33,0.33,"2018-06-28T08:35:39",{"$f":"AVERAGE(G56:G61)","v":6.9999999999999993E-2}]
[6,28,2018,8,35,49,0.63,0.63,"2018-06-28T08:35:49",0.16500000000000001]
[6,28,2018,8,35,59,0.54,0.54,"2018-06-28T08:35:59",0.245]
[6,28,2018,8,36,9,-0.51,-0.51,"2018-06-28T08:36:09",0.15000000000000002]
[6,28,2018,8,36,19,-0.51,-0.51,"2018-06-28T08:36:19",9.0000000000000011E-2]
[6,28,2018,8,36,29,-0.54,-0.54,"2018-06-28T08:36:29",-1.0000000000000009E-2]
[6,28,2018,8,36,39,-0.51,-0.51,"2018-06-28T08:36:39",-0.15000000000000002]
[6,28,2018,8,36,49,-0.51,-0.51,"2018-06-28T08:36:49",-0.34]
[6,28,2018,8,36,59,-0.48,-0.48,"2018-06-28T08:36:59",-0.51]
[6,28,2018,8,37,9,-0.48,-0.48,"2018-06-28T08:37:09",-0.505]
[6,28,2018,8,37,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T08:37:19",-0.49499999999999994]
[6,28,2018,8,37,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T08:37:29",-0.48]
[6,28,2018,8,37,39,-0.44999999999999996,-0.44999999999999996,"2018-06-28T08:37:39",-0.47000000000000003]
[6,28,2018,8,37,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T08:37:49",-0.45999999999999996]
[6,28,2018,8,37,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T08:37:59",-0.44999999999999996]
[6,28,2018,8,38,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T08:38:09",-0.43999999999999995]
[6,28,2018,8,38,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T08:38:19",-0.435]
[6,28,2018,8,38,29,-0.39,-0.39,"2018-06-28T08:38:29",-0.42499999999999999]
[6,28,2018,8,38,39,-0.36,-0.36,"2018-06-28T08:38:39",-0.41]
[6,28,2018,8,38,49,-0.54,-0.54,"2018-06-28T08:38:49",-0.42500000000000004]
[6,28,2018,8,38,59,-0.48,-0.48,"2018-06-28T08:38:59",-0.435,{"$f":"AVERAGE(G56:G81)","v":-0.26076923076923075}]
[6,28,2018,8,39,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T08:39:09",-0.43999999999999995,-0.2803846153846154]
[6,28,2018,8,39,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T08:39:19",-0.44500000000000001,-0.30000000000000004]
[6,28,2018,8,39,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T08:39:29",-0.4549999999999999,-0.31961538461538463]
[6,28,2018,8,39,39,-0.44999999999999996,-0.44999999999999996,"2018-06-28T08:39:39",-0.47000000000000003,-0.33115384615384613]
[6,28,2018,8,39,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:39:49",-0.43,-0.34500000000000003]
[6,28,2018,8,39,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:39:59",-0.39999999999999991,-0.36923076923076931]
[6,28,2018,8,40,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:40:09",-0.375,-0.40499999999999997]
[6,28,2018,8,40,19,-0.24,-0.24,"2018-06-28T08:40:19",-0.34,-0.435]
[6,28,2018,8,40,29,-0.33,-0.33,"2018-06-28T08:40:29",-0.32,-0.42807692307692313]
[6,28,2018,8,40,39,-0.27,-0.27,"2018-06-28T08:40:39",-0.29000000000000004,-0.41884615384615387]
[6,28,2018,8,40,49,-0.42000000000000004,-0.42000000000000004,"2018-06-28T08:40:49",-0.31000000000000005,-0.41423076923076929]
[6,28,2018,8,40,59,-0.44999999999999996,-0.44999999999999996,"2018-06-28T08:40:59",-0.33499999999999996,-0.411923076923077]
[6,28,2018,8,41,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T08:41:09",-0.35500000000000004,-0.40846153846153843]
[6,28,2018,8,41,19,-0.39,-0.39,"2018-06-28T08:41:19",-0.38000000000000006,-0.40500000000000003]
[6,28,2018,8,41,29,-0.42000000000000004,-0.42000000000000004,"2018-06-28T08:41:29",-0.39500000000000002,-0.40269230769230763]
[6,28,2018,8,41,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T08:41:39",-0.42,-0.40153846153846151]
[6,28,2018,8,41,49,-0.27,-0.27,"2018-06-28T08:41:49",-0.39500000000000002,-0.39461538461538459]
[6,28,2018,8,41,59,-0.27,-0.27,"2018-06-28T08:41:59",-0.36499999999999999,-0.38769230769230767]
[6,28,2018,8,42,9,-0.27,-0.27,"2018-06-28T08:42:09",-0.34,-0.38076923076923069]
[6,28,2018,8,42,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:42:19",-0.32500000000000001,-0.37615384615384612]
[6,28,2018,8,42,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:42:29",-0.30499999999999999,-0.37153846153846154]
[6,28,2018,8,42,39,-0.27,-0.27,"2018-06-28T08:42:39",-0.28000000000000003,-0.36576923076923074]
[6,28,2018,8,42,49,-0.27,-0.27,"2018-06-28T08:42:49",-0.28000000000000003,-0.3611538461538461]
[6,28,2018,8,42,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:42:59",-0.28500000000000003,-0.35884615384615387]
[6,28,2018,8,43,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:43:09",-0.29000000000000004,-0.34961538461538455]
[6,28,2018,8,43,19,-0.27,-0.27,"2018-06-28T08:43:19",-0.28500000000000003,-0.34153846153846146]
[6,28,2018,8,43,29,-0.27,-0.27,"2018-06-28T08:43:29",-0.28000000000000003,-0.33461538461538443]
[6,28,2018,8,43,39,-0.24,-0.24,"2018-06-28T08:43:39",-0.27500000000000002,-0.32653846153846139]
[6,28,2018,8,43,49,-0.24,-0.24,"2018-06-28T08:43:49",-0.27,-0.31846153846153835]
[6,28,2018,8,43,59,-0.24,-0.24,"2018-06-28T08:43:59",-0.26,-0.31038461538461531]
[6,28,2018,8,44,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T08:44:09",-0.245,-0.30692307692307685]
[6,28,2018,8,44,19,-0.18,-0.18,"2018-06-28T08:44:19",-0.22999999999999998,-0.30230769230769217]
[6,28,2018,8,44,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T08:44:29",-0.21999999999999997,-0.29884615384615376]
[6,28,2018,8,44,39,-0.18,-0.18,"2018-06-28T08:44:39",-0.20999999999999996,-0.29653846153846153]
[6,28,2018,8,44,49,-0.18,-0.18,"2018-06-28T08:44:49",-0.19999999999999998,-0.29076923076923072]
[6,28,2018,8,44,59,-0.12,-0.12,"2018-06-28T08:44:59",-0.18000000000000002,-0.28499999999999992]
[6,28,2018,8,45,9,-0.12,-0.12,"2018-06-28T08:45:09",-0.16500000000000001,-0.27346153846153842]
[6,28,2018,8,45,19,-0.09,-0.09,"2018-06-28T08:45:19",-0.15,-0.25961538461538453]
[6,28,2018,8,45,29,-0.09,-0.09,"2018-06-28T08:45:29",-0.12999999999999998,-0.24692307692307686]
[6,28,2018,8,45,39,-0.12,-0.12,{"$f":"DATE(C121,A121,B121)+TIME(D121,E121,F121)","v":"2018-06-28T08:45:39"},-0.12,-0.23653846153846153]
[6,28,2018,8,45,49,-0.09,-0.09,"2018-06-28T08:45:49",-0.10499999999999998,-0.22384615384615383]
[6,28,2018,8,45,59,-0.09,-0.09,"2018-06-28T08:45:59",-9.9999999999999992E-2,-0.21115384615384614]
[6,28,2018,8,46,9,-0.09,-0.09,"2018-06-28T08:46:09",-9.4999999999999987E-2,-0.20423076923076924]
[6,28,2018,8,46,19,-0.12,-0.12,"2018-06-28T08:46:19",{"$f":"AVERAGE(G120:G125)","v":-9.9999999999999992E-2},-0.19846153846153847]
[6,28,2018,8,46,29,-0.09,-0.09,"2018-06-28T08:46:29",-9.9999999999999992E-2,-0.19153846153846155]
[6,28,2018,8,46,39,-0.12,-0.12,"2018-06-28T08:46:39",-9.9999999999999992E-2,-0.18461538461538465]
[6,28,2018,8,46,49,0,0,"2018-06-28T08:46:49",-8.5000000000000006E-2,-0.1730769230769231]
[6,28,2018,8,46,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T08:46:59",-0.105,-0.17076923076923076]
[6,28,2018,8,47,9,-0.18,-0.18,"2018-06-28T08:47:09",-0.12,-0.16730769230769232]
[6,28,2018,8,47,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T08:47:19",-0.12500000000000003,-0.16153846153846155]
[6,28,2018,8,47,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T08:47:29",-0.13500000000000001,-0.15576923076923077]
[6,28,2018,8,47,39,-0.18,-0.18,"2018-06-28T08:47:39",-0.14500000000000002,-0.15230769230769228]
[6,28,2018,8,47,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T08:47:49",-0.18000000000000002,-0.14999999999999997]
[6,28,2018,8,47,59,-0.24,-0.24,"2018-06-28T08:47:59",-0.18500000000000003,-0.14999999999999997]
[6,28,2018,8,48,9,-0.24,-0.24,"2018-06-28T08:48:09",-0.19499999999999998,-0.15000000000000002]
[6,28,2018,8,48,19,-0.24,-0.24,"2018-06-28T08:48:19",-0.21,-0.15000000000000005]
[6,28,2018,8,48,29,-0.27,-0.27,"2018-06-28T08:48:29",-0.22999999999999998,-0.15230769230769231]
[6,28,2018,8,48,39,-0.24,-0.24,"2018-06-28T08:48:39",-0.24,-0.15461538461538463]
[6,28,2018,8,48,49,-0.27,-0.27,"2018-06-28T08:48:49",-0.25,-0.15692307692307692]
[6,28,2018,8,48,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:48:59",-0.26,-0.16153846153846155]
[6,28,2018,8,49,9,-0.27,-0.27,"2018-06-28T08:49:09",-0.26500000000000001,-0.16500000000000004]
[6,28,2018,8,49,19,-0.27,-0.27,"2018-06-28T08:49:19",-0.27,-0.17076923076923076]
[6,28,2018,8,49,29,-0.24,-0.24,"2018-06-28T08:49:29",-0.26500000000000001,-0.17538461538461542]
[6,28,2018,8,49,39,-0.27,-0.27,"2018-06-28T08:49:39",-0.27,{"$f":"AVERAGE(G120:G145)","v":-0.18230769230769231}]
[6,28,2018,8,49,49,-0.24,-0.24,"2018-06-28T08:49:49",-0.26500000000000001,-0.18807692307692309]
[6,28,2018,8,49,59,-0.27,-0.27,"2018-06-28T08:49:59",-0.26,-0.19384615384615389]
[6,28,2018,8,50,9,-0.24,-0.24,"2018-06-28T08:50:09",-0.255,-0.19961538461538458]
[6,28,2018,8,50,19,-0.27,-0.27,"2018-06-28T08:50:19",-0.255,-0.2065384615384615]
[6,28,2018,8,50,29,-0.27,-0.27,"2018-06-28T08:50:29",-0.26,-0.21346153846153842]
[6,28,2018,8,50,39,-0.27,-0.27,"2018-06-28T08:50:39",-0.26,-0.2192307692307692]
[6,28,2018,8,50,49,-0.27,-0.27,"2018-06-28T08:50:49",-0.26500000000000001,-0.22615384615384612]
[6,28,2018,8,50,59,-0.27,-0.27,"2018-06-28T08:50:59",-0.26500000000000001,-0.2319230769230769]
[6,28,2018,8,51,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:51:09",-0.27500000000000002,-0.24346153846153842]
[6,28,2018,8,51,19,-0.33,-0.33,"2018-06-28T08:51:19",-0.28500000000000003,-0.24807692307692303]
[6,28,2018,8,51,29,-0.36,-0.36,"2018-06-28T08:51:29",-0.30000000000000004,-0.25499999999999995]
[6,28,2018,8,51,39,-0.33,-0.33,"2018-06-28T08:51:39",-0.31000000000000005,-0.26192307692307687]
[6,28,2018,8,51,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:51:49",-0.31500000000000006,-0.26769230769230762]
[6,28,2018,8,51,59,-0.33,-0.33,"2018-06-28T08:51:59",-0.32500000000000001,-0.27346153846153842]
[6,28,2018,8,52,9,-0.33,-0.33,"2018-06-28T08:52:09",-0.33,-0.27807692307692305]
[6,28,2018,8,52,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:52:19",-0.32500000000000001,-0.28038461538461534]
[6,28,2018,8,52,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:52:29",-0.31500000000000006,-0.28269230769230769]
[6,28,2018,8,52,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:52:39",-0.31000000000000005,-0.28500000000000003]
[6,28,2018,8,52,49,-0.27,-0.27,"2018-06-28T08:52:49",-0.30500000000000005,-0.28500000000000003]
[6,28,2018,8,52,59,-0.27,-0.27,"2018-06-28T08:52:59",-0.29500000000000004,-0.28615384615384615]
[6,28,2018,8,53,9,-0.27,-0.27,"2018-06-28T08:53:09",-0.28500000000000003,-0.28615384615384615]
[6,28,2018,8,53,19,-0.24,-0.24,"2018-06-28T08:53:19",-0.27500000000000002,-0.2838461538461538]
[6,28,2018,8,53,29,-0.24,-0.24,"2018-06-28T08:53:29",-0.26500000000000001,-0.28269230769230769]
[6,28,2018,8,53,39,-0.27,-0.27,"2018-06-28T08:53:39",-0.26,-0.28269230769230769]
[6,28,2018,8,53,49,-0.24,-0.24,"2018-06-28T08:53:49",-0.255,-0.28269230769230769]
[6,28,2018,8,53,59,-0.24,-0.24,"2018-06-28T08:53:59",-0.25,-0.28153846153846157]
[6,28,2018,8,54,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T08:54:09",-0.24,-0.2803846153846154]
[6,28,2018,8,54,19,-0.18,-0.18,"2018-06-28T08:54:19",-0.22999999999999998,-0.27692307692307688]
[6,28,2018,8,54,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T08:54:29",-0.215,-0.27346153846153848]
[6,28,2018,8,54,39,-0.12,-0.12,"2018-06-28T08:54:39",-0.19000000000000003,-0.26769230769230767]
[6,28,2018,8,54,49,-0.09,-0.09,"2018-06-28T08:54:49",-0.16500000000000001,-0.26076923076923075]
[6,28,2018,8,54,59,-0.09,-0.09,"2018-06-28T08:54:59",-0.13999999999999999,-0.25384615384615383]
[6,28,2018,8,55,9,-0.06,-0.06,"2018-06-28T08:55:09",-0.11499999999999999,-0.24576923076923077]
[6,28,2018,8,55,19,-0.09,-0.09,"2018-06-28T08:55:19",-9.9999999999999992E-2,-0.23884615384615385]
[6,28,2018,8,55,29,-0.06,-0.06,"2018-06-28T08:55:29",-8.5000000000000006E-2,-0.22961538461538458]
[6,28,2018,8,55,39,-0.12,-0.12,"2018-06-28T08:55:39",-8.5000000000000006E-2,-0.22153846153846149]
[6,28,2018,8,55,49,-0.09,-0.09,"2018-06-28T08:55:49",-8.5000000000000006E-2,-0.21115384615384614]
[6,28,2018,8,55,59,-0.12,-0.12,"2018-06-28T08:55:59",-8.9999999999999983E-2,-0.20307692307692304]
[6,28,2018,8,56,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T08:56:09",-0.105,-0.1973076923076923]
[6,28,2018,8,56,19,-0.18,-0.18,{"$f":"DATE(C185,A185,B185)+TIME(D185,E185,F185)","v":"2018-06-28T08:56:19"},-0.12,-0.19153846153846152]
[6,28,2018,8,56,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T08:56:29",-0.14499999999999999,-0.18692307692307694]
[6,28,2018,8,56,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T08:56:39",-0.16,-0.18346153846153848]
[6,28,2018,8,56,49,-0.24,-0.24,"2018-06-28T08:56:49",-0.18500000000000003,-0.18115384615384617]
[6,28,2018,8,56,59,-0.24,-0.24,"2018-06-28T08:56:59",{"$f":"AVERAGE(G184:G189)","v":-0.20499999999999999},-0.17884615384615385]
[6,28,2018,8,57,9,-0.27,-0.27,"2018-06-28T08:57:09",-0.22500000000000001,-0.17884615384615385]
[6,28,2018,8,57,19,-0.27,-0.27,"2018-06-28T08:57:19",-0.24,-0.17884615384615385]
[6,28,2018,8,57,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:57:29",-0.255,-0.18000000000000002]
[6,28,2018,8,57,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:57:39",-0.27,-0.18230769230769231]
[6,28,2018,8,57,49,-0.48,-0.48,"2018-06-28T08:57:49",-0.31,-0.19153846153846155]
[6,28,2018,8,57,59,-0.48,-0.48,"2018-06-28T08:57:59",-0.35000000000000003,-0.19961538461538467]
[6,28,2018,8,58,9,-0.51,-0.51,"2018-06-28T08:58:09",-0.38999999999999996,-0.21000000000000002]
[6,28,2018,8,58,19,-0.51,-0.51,"2018-06-28T08:58:19",-0.43,-0.2203846153846154]
[6,28,2018,8,58,29,-0.54,-0.54,"2018-06-28T08:58:29",-0.47000000000000003,-0.23307692307692307]
[6,28,2018,8,58,39,-0.51,-0.51,"2018-06-28T08:58:39",-0.505,-0.24576923076923071]
[6,28,2018,8,58,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:58:49",-0.47499999999999992,-0.25153846153846149]
[6,28,2018,8,58,59,-0.33,-0.33,"2018-06-28T08:58:59",-0.45,-0.25961538461538458]
[6,28,2018,8,59,9,-0.36,-0.36,"2018-06-28T08:59:09",-0.42499999999999999,-0.26999999999999996]
[6,28,2018,8,59,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T08:59:19",-0.38999999999999996,-0.27807692307692305]
[6,28,2018,8,59,29,-0.42000000000000004,-0.42000000000000004,"2018-06-28T08:59:29",-0.37000000000000005,-0.2919230769230769]
[6,28,2018,8,59,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T08:59:39",-0.35499999999999998,-0.30461538461538457]
[6,28,2018,8,59,49,-0.42000000000000004,-0.42000000000000004,"2018-06-28T08:59:49",-0.375,-0.31846153846153846]
[6,28,2018,8,59,59,-0.44999999999999996,-0.44999999999999996,"2018-06-28T08:59:59",-0.39500000000000002,-0.33115384615384613]
[6,28,2018,9,0,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:00:09",-0.41,-0.34499999999999997]
[6,28,2018,9,0,19,-0.48,-0.48,"2018-06-28T09:00:19",-0.44,{"$f":"AVERAGE(G184:G209)","v":-0.35884615384615376}]
[6,28,2018,9,0,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:00:29",-0.44500000000000001,-0.37038461538461537]
[6,28,2018,9,0,39,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:00:39",-0.45,-0.38076923076923064]
[6,28,2018,9,0,49,-0.48,-0.48,"2018-06-28T09:00:49",-0.45999999999999996,-0.39115384615384607]
[6,28,2018,9,0,59,-0.48,-0.48,"2018-06-28T09:00:59",-0.46499999999999991,-0.40153846153846151]
[6,28,2018,9,1,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:01:09",-0.46500000000000002,-0.40961538461538455]
[6,28,2018,9,1,19,-0.48,-0.48,"2018-06-28T09:01:19",-0.46499999999999991,-0.41884615384615381]
[6,28,2018,9,1,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:01:29",-0.46500000000000002,-0.42576923076923073]
[6,28,2018,9,1,39,-0.51,-0.51,"2018-06-28T09:01:39",-0.47499999999999992,-0.43499999999999994]
[6,28,2018,9,1,49,-0.48,-0.48,"2018-06-28T09:01:49",-0.47500000000000003,-0.44192307692307692]
[6,28,2018,9,1,59,-0.51,-0.51,"2018-06-28T09:01:59",-0.48,-0.45000000000000007]
[6,28,2018,9,2,9,-0.51,-0.51,"2018-06-28T09:02:09",-0.48999999999999994,-0.45115384615384618]
[6,28,2018,9,2,19,-0.51,-0.51,"2018-06-28T09:02:19",-0.49499999999999994,-0.4523076923076923]
[6,28,2018,9,2,29,-0.51,-0.51,"2018-06-28T09:02:29",-0.50499999999999989,-0.4523076923076923]
[6,28,2018,9,2,39,-0.48,-0.48,"2018-06-28T09:02:39",-0.49999999999999994,-0.45115384615384618]
[6,28,2018,9,2,49,-0.48,-0.48,"2018-06-28T09:02:49",-0.5,-0.44884615384615389]
[6,28,2018,9,2,59,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:02:59",-0.48999999999999994,-0.4465384615384615]
[6,28,2018,9,3,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:03:09",-0.47499999999999992,-0.45115384615384613]
[6,28,2018,9,3,19,-0.39,-0.39,"2018-06-28T09:03:19",-0.45500000000000002,-0.45346153846153842]
[6,28,2018,9,3,29,-0.39,-0.39,"2018-06-28T09:03:29",-0.43500000000000005,-0.45461538461538464]
[6,28,2018,9,3,39,-0.39,-0.39,"2018-06-28T09:03:39",-0.4200000000000001,-0.4580769230769231]
[6,28,2018,9,3,49,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:03:49",-0.41,-0.4580769230769231]
[6,28,2018,9,3,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:03:59",-0.40500000000000003,-0.4580769230769231]
[6,28,2018,9,4,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:04:09",-0.40499999999999997,-0.4580769230769231]
[6,28,2018,9,4,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:04:19",-0.41500000000000004,-0.45807692307692299]
[6,28,2018,9,4,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:04:29",-0.42499999999999999,-0.45807692307692299]
[6,28,2018,9,4,39,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:04:39",-0.43500000000000005,-0.45692307692307688]
[6,28,2018,9,4,49,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:04:49",-0.435,-0.4557692307692307]
[6,28,2018,9,4,59,-0.39,-0.39,"2018-06-28T09:04:59",-0.43,-0.45346153846153836]
[6,28,2018,9,5,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:05:09",-0.43,-0.45115384615384602]
[6,28,2018,9,5,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:05:19",-0.42499999999999999,-0.44884615384615373]
[6,28,2018,9,5,29,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:05:29",-0.42,-0.44769230769230756]
[6,28,2018,9,5,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:05:39",-0.41499999999999998,-0.44538461538461527]
[6,28,2018,9,5,49,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:05:49",-0.41499999999999998,-0.4442307692307691]
[6,28,2018,9,5,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:05:59",-0.42,-0.44076923076923075]
[6,28,2018,9,6,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:06:09",-0.42499999999999999,-0.43961538461538463]
[6,28,2018,9,6,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:06:19",-0.43,-0.43730769230769223]
[6,28,2018,9,6,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:06:29",-0.43500000000000005,-0.43499999999999989]
[6,28,2018,9,6,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:06:39",-0.435,-0.43153846153846148]
[6,28,2018,9,6,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:06:49",-0.43999999999999995,-0.42923076923076919]
[6,28,2018,9,6,59,-0.48,-0.48,{"$f":"DATE(C249,A249,B249)+TIME(D249,E249,F249)","v":"2018-06-28T09:06:59"},-0.44999999999999996,-0.42923076923076919]
[6,28,2018,9,7,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:07:09",-0.45,-0.42807692307692297]
[6,28,2018,9,7,19,-0.48,-0.48,"2018-06-28T09:07:19",-0.45500000000000002,-0.42923076923076919]
[6,28,2018,9,7,29,-0.51,-0.51,"2018-06-28T09:07:29",-0.46500000000000002,-0.4326923076923076]
[6,28,2018,9,7,39,-0.51,-0.51,"2018-06-28T09:07:39",{"$f":"AVERAGE(G248:G253)","v":-0.48},-0.43730769230769229]
[6,28,2018,9,7,49,-0.54,-0.54,"2018-06-28T09:07:49",-0.49499999999999994,-0.44307692307692303]
[6,28,2018,9,7,59,-0.51,-0.51,"2018-06-28T09:07:59",-0.5,-0.44769230769230767]
[6,28,2018,9,8,9,-0.51,-0.51,"2018-06-28T09:08:09",-0.5099999999999999,-0.45115384615384618]
[6,28,2018,9,8,19,-0.51,-0.51,"2018-06-28T09:08:19",-0.51500000000000001,-0.45461538461538453]
[6,28,2018,9,8,29,-0.51,-0.51,"2018-06-28T09:08:29",-0.51500000000000001,-0.4580769230769231]
[6,28,2018,9,8,39,-0.51,-0.51,"2018-06-28T09:08:39",-0.51500000000000001,-0.46038461538461528]
[6,28,2018,9,8,49,-0.51,-0.51,"2018-06-28T09:08:49",-0.5099999999999999,-0.46269230769230763]
[6,28,2018,9,8,59,-0.54,-0.54,"2018-06-28T09:08:59",-0.51500000000000001,-0.46615384615384603]
[6,28,2018,9,9,9,-0.57000000000000006,-0.57000000000000006,"2018-06-28T09:09:09",-0.52500000000000002,-0.47192307692307678]
[6,28,2018,9,9,19,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:09:19",-0.54000000000000015,-0.47999999999999993]
[6,28,2018,9,9,29,-0.57000000000000006,-0.57000000000000006,"2018-06-28T09:09:29",-0.54999999999999993,-0.48576923076923079]
[6,28,2018,9,9,39,-0.54,-0.54,"2018-06-28T09:09:39",-0.55500000000000005,-0.49038461538461536]
[6,28,2018,9,9,49,-0.54,-0.54,"2018-06-28T09:09:49",-0.56000000000000005,-0.49500000000000005]
[6,28,2018,9,9,59,-0.54,-0.54,"2018-06-28T09:09:59",-0.56000000000000005,-0.49961538461538457]
[6,28,2018,9,10,9,-0.51,-0.51,"2018-06-28T09:10:09",-0.54999999999999993,-0.50307692307692298]
[6,28,2018,9,10,19,-0.51,-0.51,"2018-06-28T09:10:19",-0.53500000000000003,-0.50653846153846149]
[6,28,2018,9,10,29,-0.48,-0.48,"2018-06-28T09:10:29",-0.51999999999999991,-0.50769230769230766]
[6,28,2018,9,10,39,-0.48,-0.48,"2018-06-28T09:10:39",-0.51,-0.50884615384615373]
[6,28,2018,9,10,49,-0.54,-0.54,"2018-06-28T09:10:49",-0.51,-0.51230769230769213]
[6,28,2018,9,10,59,-0.54,-0.54,"2018-06-28T09:10:59",-0.51,{"$f":"AVERAGE(G248:G273)","v":-0.51692307692307682}]
[6,28,2018,9,11,9,-0.51,-0.51,"2018-06-28T09:11:09",-0.5099999999999999,-0.51923076923076905]
[6,28,2018,9,11,19,-0.48,-0.48,"2018-06-28T09:11:19",-0.505,-0.51923076923076916]
[6,28,2018,9,11,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:11:29",-0.5,-0.51923076923076916]
[6,28,2018,9,11,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:11:39",-0.49000000000000005,-0.51692307692307682]
[6,28,2018,9,11,49,-0.36,-0.36,"2018-06-28T09:11:49",-0.45999999999999996,-0.51115384615384607]
[6,28,2018,9,11,59,-0.33,-0.33,"2018-06-28T09:11:59",-0.42499999999999999,-0.50423076923076926]
[6,28,2018,9,12,9,-0.33,-0.33,"2018-06-28T09:12:09",-0.39500000000000002,-0.49615384615384611]
[6,28,2018,9,12,19,-0.39,-0.39,"2018-06-28T09:12:19",-0.38000000000000006,-0.49153846153846142]
[6,28,2018,9,12,29,-0.36,-0.36,"2018-06-28T09:12:29",-0.36499999999999999,-0.48576923076923073]
[6,28,2018,9,12,39,-0.36,-0.36,"2018-06-28T09:12:39",-0.35499999999999998,-0.47999999999999993]
[6,28,2018,9,12,49,-0.36,-0.36,"2018-06-28T09:12:49",-0.35499999999999998,-0.47423076923076918]
[6,28,2018,9,12,59,-0.39,-0.39,"2018-06-28T09:12:59",-0.36499999999999999,-0.4696153846153846]
[6,28,2018,9,13,9,-0.36,-0.36,"2018-06-28T09:13:09",-0.36999999999999994,-0.4638461538461538]
[6,28,2018,9,13,19,-0.39,-0.39,"2018-06-28T09:13:19",-0.37000000000000005,-0.4580769230769231]
[6,28,2018,9,13,29,-0.39,-0.39,"2018-06-28T09:13:29",-0.375,-0.45115384615384618]
[6,28,2018,9,13,39,-0.39,-0.39,"2018-06-28T09:13:39",-0.38000000000000006,-0.44307692307692315]
[6,28,2018,9,13,49,-0.39,-0.39,"2018-06-28T09:13:49",-0.38500000000000006,-0.43615384615384623]
[6,28,2018,9,13,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:13:59",-0.39000000000000007,-0.43153846153846165]
[6,28,2018,9,14,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:14:09",-0.39999999999999997,-0.42692307692307707]
[6,28,2018,9,14,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:14:19",-0.41,-0.42346153846153861]
[6,28,2018,9,14,29,-0.48,-0.48,"2018-06-28T09:14:29",-0.42500000000000004,-0.42230769230769238]
[6,28,2018,9,14,39,-0.48,-0.48,"2018-06-28T09:14:39",-0.44,-0.42115384615384621]
[6,28,2018,9,14,49,-0.54,-0.54,"2018-06-28T09:14:49",-0.46500000000000002,-0.42346153846153839]
[6,28,2018,9,14,59,-0.54,-0.54,"2018-06-28T09:14:59",-0.48500000000000004,-0.42576923076923079]
[6,28,2018,9,15,9,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:15:09",-0.51500000000000001,-0.42807692307692297]
[6,28,2018,9,15,19,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:15:19",-0.54,-0.43038461538461531]
[6,28,2018,9,15,29,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:15:29",-0.56000000000000005,-0.43384615384615366]
[6,28,2018,9,15,39,-0.57000000000000006,-0.57000000000000006,"2018-06-28T09:15:39",-0.57500000000000007,-0.43730769230769229]
[6,28,2018,9,15,49,-0.57000000000000006,-0.57000000000000006,"2018-06-28T09:15:49",-0.58000000000000007,-0.44192307692307681]
[6,28,2018,9,15,59,-0.57000000000000006,-0.57000000000000006,"2018-06-28T09:15:59",-0.58500000000000008,-0.44769230769230767]
[6,28,2018,9,16,9,-0.57000000000000006,-0.57000000000000006,"2018-06-28T09:16:09",-0.58000000000000007,-0.45576923076923076]
[6,28,2018,9,16,19,-0.57000000000000006,-0.57000000000000006,"2018-06-28T09:16:19",-0.57500000000000018,-0.46500000000000008]
[6,28,2018,9,16,29,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:16:29",-0.57500000000000007,-0.47538461538461541]
[6,28,2018,9,16,39,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:16:39",-0.58000000000000007,-0.4834615384615385]
[6,28,2018,9,16,49,-0.78,-0.78,"2018-06-28T09:16:49",-0.6150000000000001,-0.49961538461538463]
[6,28,2018,9,16,59,-0.78,-0.78,"2018-06-28T09:16:59",-0.65,-0.51576923076923076]
[6,28,2018,9,17,9,-0.78,-0.78,"2018-06-28T09:17:09",-0.68500000000000005,-0.53192307692307683]
[6,28,2018,9,17,19,-0.75,-0.75,"2018-06-28T09:17:19",-0.71499999999999997,-0.54576923076923067]
[6,28,2018,9,17,29,-0.72,-0.72,"2018-06-28T09:17:29",-0.73499999999999999,-0.55961538461538463]
[6,28,2018,9,17,39,-0.66,-0.66,{"$f":"DATE(C313,A313,B313)+TIME(D313,E313,F313)","v":"2018-06-28T09:17:39"},-0.745,-0.56999999999999995]
[6,28,2018,9,17,49,-0.33,-0.33,"2018-06-28T09:17:49",-0.67,-0.56769230769230772]
[6,28,2018,9,17,59,-0.33,-0.33,"2018-06-28T09:17:59",-0.59500000000000008,-0.56538461538461537]
[6,28,2018,9,18,9,-0.33,-0.33,"2018-06-28T09:18:09",-0.52,-0.56307692307692314]
[6,28,2018,9,18,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T09:18:19",{"$f":"AVERAGE(G312:G317)","v":-0.44500000000000001},-0.55846153846153856]
[6,28,2018,9,18,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T09:18:29",-0.375,-0.55384615384615388]
[6,28,2018,9,18,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T09:18:39",-0.315,-0.54807692307692313]
[6,28,2018,9,18,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:18:49",-0.33500000000000002,-0.54692307692307707]
[6,28,2018,9,18,59,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:18:59",-0.35499999999999998,-0.5457692307692309]
[6,28,2018,9,19,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:19:09",-0.37000000000000005,-0.54115384615384621]
[6,28,2018,9,19,19,-0.39,-0.39,"2018-06-28T09:19:19",-0.38500000000000001,-0.53538461538461557]
[6,28,2018,9,19,29,-0.36,-0.36,"2018-06-28T09:19:29",-0.39500000000000002,-0.52615384615384619]
[6,28,2018,9,19,39,-0.36,-0.36,"2018-06-28T09:19:39",-0.40499999999999997,-0.51692307692307693]
[6,28,2018,9,19,49,-0.36,-0.36,"2018-06-28T09:19:49",-0.38999999999999996,-0.50769230769230778]
[6,28,2018,9,19,59,-0.33,-0.33,"2018-06-28T09:19:59",-0.36999999999999994,-0.49846153846153851]
[6,28,2018,9,20,9,-0.36,-0.36,"2018-06-28T09:20:09",-0.35999999999999993,-0.49038461538461536]
[6,28,2018,9,20,19,-0.36,-0.36,"2018-06-28T09:20:19",-0.35499999999999998,-0.48230769230769227]
[6,28,2018,9,20,29,-0.36,-0.36,"2018-06-28T09:20:29",-0.35499999999999998,-0.47423076923076912]
[6,28,2018,9,20,39,-0.36,-0.36,"2018-06-28T09:20:39",-0.35499999999999993,-0.46615384615384597]
[6,28,2018,9,20,49,-0.36,-0.36,"2018-06-28T09:20:49",-0.35499999999999993,-0.45692307692307682]
[6,28,2018,9,20,59,-0.36,-0.36,"2018-06-28T09:20:59",-0.35999999999999993,-0.4476923076923075]
[6,28,2018,9,21,9,-0.36,-0.36,"2018-06-28T09:21:09",-0.35999999999999993,-0.43153846153846137]
[6,28,2018,9,21,19,-0.39,-0.39,"2018-06-28T09:21:19",-0.36499999999999999,-0.41653846153846147]
[6,28,2018,9,21,29,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:21:29",-0.375,-0.40269230769230763]
[6,28,2018,9,21,39,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:21:39",-0.38999999999999996,{"$f":"AVERAGE(G312:G337)","v":-0.39115384615384613}]
[6,28,2018,9,21,49,-0.48,-0.48,"2018-06-28T09:21:49",-0.41,-0.38192307692307703]
[6,28,2018,9,21,59,-0.48,-0.48,"2018-06-28T09:21:59",-0.42999999999999994,-0.37500000000000011]
[6,28,2018,9,22,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:22:09",-0.43999999999999995,-0.37846153846153852]
[6,28,2018,9,22,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:22:19",-0.44500000000000001,-0.38192307692307698]
[6,28,2018,9,22,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:22:29",-0.45,-0.38653846153846155]
[6,28,2018,9,22,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:22:39",-0.44500000000000001,-0.39115384615384624]
[6,28,2018,9,22,49,-0.36,-0.36,"2018-06-28T09:22:49",-0.42499999999999999,-0.39346153846153847]
[6,28,2018,9,22,59,-0.33,-0.33,"2018-06-28T09:22:59",-0.39999999999999997,-0.39461538461538459]
[6,28,2018,9,23,9,-0.36,-0.36,"2018-06-28T09:23:09",-0.38999999999999996,-0.39115384615384607]
[6,28,2018,9,23,19,-0.33,-0.33,"2018-06-28T09:23:19",-0.375,-0.3865384615384615]
[6,28,2018,9,23,29,-0.33,-0.33,"2018-06-28T09:23:29",-0.35500000000000004,-0.38307692307692304]
[6,28,2018,9,23,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T09:23:39",-0.33499999999999996,-0.37961538461538463]
[6,28,2018,9,23,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T09:23:49",-0.32500000000000001,-0.3773076923076924]
[6,28,2018,9,23,59,-0.27,-0.27,"2018-06-28T09:23:59",-0.315,-0.37384615384615388]
[6,28,2018,9,24,9,-0.24,-0.24,"2018-06-28T09:24:09",-0.29500000000000004,-0.36923076923076931]
[6,28,2018,9,24,19,-0.24,-0.24,"2018-06-28T09:24:19",-0.28000000000000003,-0.36576923076923085]
[6,28,2018,9,24,29,-0.27,-0.27,"2018-06-28T09:24:29",-0.27,-0.36230769230769239]
[6,28,2018,9,24,39,-0.33,-0.33,"2018-06-28T09:24:39",-0.27500000000000002,-0.36115384615384616]
[6,28,2018,9,24,49,-0.33,-0.33,"2018-06-28T09:24:49",-0.28000000000000003,-0.36000000000000004]
[6,28,2018,9,24,59,-0.39,-0.39,"2018-06-28T09:24:59",-0.30000000000000004,-0.36115384615384616]
[6,28,2018,9,25,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:25:09",-0.33499999999999996,-0.36461538461538462]
[6,28,2018,9,25,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:25:19",-0.36500000000000005,-0.36692307692307691]
[6,28,2018,9,25,29,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:25:29",-0.38999999999999996,-0.3692307692307692]
[6,28,2018,9,25,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:25:39",-0.40499999999999997,-0.37038461538461537]
[6,28,2018,9,25,49,-0.39,-0.39,"2018-06-28T09:25:49",-0.41500000000000004,-0.3692307692307692]
[6,28,2018,9,25,59,-0.33,-0.33,"2018-06-28T09:25:59",-0.40500000000000003,-0.36461538461538462]
[6,28,2018,9,26,9,-0.39,-0.39,"2018-06-28T09:26:09",-0.39500000000000007,-0.36115384615384616]
[6,28,2018,9,26,19,-0.36,-0.36,"2018-06-28T09:26:19",-0.38500000000000001,-0.35653846153846153]
[6,28,2018,9,26,29,-0.36,-0.36,"2018-06-28T09:26:29",-0.375,-0.35423076923076913]
[6,28,2018,9,26,39,-0.39,-0.39,"2018-06-28T09:26:39",-0.36999999999999994,-0.35307692307692301]
[6,28,2018,9,26,49,-0.36,-0.36,"2018-06-28T09:26:49",-0.36499999999999999,-0.34961538461538461]
[6,28,2018,9,26,59,-0.36,-0.36,"2018-06-28T09:26:59",-0.36999999999999994,-0.34730769230769226]
[6,28,2018,9,27,9,-0.33,-0.33,"2018-06-28T09:27:09",-0.35999999999999993,-0.34615384615384615]
[6,28,2018,9,27,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T09:27:19",-0.34999999999999992,-0.34500000000000003]
[6,28,2018,9,27,29,-0.27,-0.27,"2018-06-28T09:27:29",-0.33499999999999996,-0.34153846153846157]
[6,28,2018,9,27,39,-0.27,-0.27,"2018-06-28T09:27:39",-0.315,-0.33923076923076922]
[6,28,2018,9,27,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T09:27:49",-0.28999999999999998,-0.33461538461538465]
[6,28,2018,9,27,59,-0.18,-0.18,"2018-06-28T09:27:59",-0.26,-0.33]
[6,28,2018,9,28,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T09:28:09",-0.22999999999999998,-0.32423076923076927]
[6,28,2018,9,28,19,-0.12,-0.12,{"$f":"DATE(C377,A377,B377)+TIME(D377,E377,F377)","v":"2018-06-28T09:28:19"},-0.20000000000000004,-0.31846153846153846]
[6,28,2018,9,28,29,-0.03,-0.03,"2018-06-28T09:28:29",-0.16,-0.31038461538461537]
[6,28,2018,9,28,39,0,0,"2018-06-28T09:28:39",-0.115,-0.30115384615384622]
[6,28,2018,9,28,49,-0.03,-0.03,"2018-06-28T09:28:49",-8.5000000000000006E-2,-0.29192307692307701]
[6,28,2018,9,28,59,0.03,0.03,"2018-06-28T09:28:59",{"$f":"AVERAGE(G376:G381)","v":-5.000000000000001E-2},-0.27807692307692305]
[6,28,2018,9,29,9,0.03,0.03,"2018-06-28T09:29:09",-0.02,-0.26423076923076927]
[6,28,2018,9,29,19,0.09,0.09,"2018-06-28T09:29:19",1.4999999999999999E-2,-0.2457692307692308]
[6,28,2018,9,29,29,0.09,0.09,"2018-06-28T09:29:29",3.4999999999999996E-2,-0.22499999999999998]
[6,28,2018,9,29,39,0.12,0.12,"2018-06-28T09:29:39",5.4999999999999993E-2,-0.20423076923076922]
[6,28,2018,9,29,49,0.12,0.12,"2018-06-28T09:29:49",0.08,-0.18346153846153845]
[6,28,2018,9,29,59,0.12,0.12,"2018-06-28T09:29:59",9.4999999999999987E-2,-0.16269230769230766]
[6,28,2018,9,30,9,0.12,0.12,"2018-06-28T09:30:09",0.11,-0.14307692307692307]
[6,28,2018,9,30,19,0.12,0.12,"2018-06-28T09:30:19",0.11499999999999999,-0.12576923076923074]
[6,28,2018,9,30,29,0.15000000000000002,0.15000000000000002,"2018-06-28T09:30:29",0.125,-0.105]
[6,28,2018,9,30,39,0.09,0.09,"2018-06-28T09:30:39",0.12,-8.7692307692307681E-2]
[6,28,2018,9,30,49,0.12,0.12,"2018-06-28T09:30:49",0.12,-6.9230769230769221E-2]
[6,28,2018,9,30,59,0.09,0.09,"2018-06-28T09:30:59",0.11499999999999999,-5.0769230769230775E-2]
[6,28,2018,9,31,9,0.09,0.09,"2018-06-28T09:31:09",0.10999999999999999,-3.3461538461538459E-2]
[6,28,2018,9,31,19,0.06,0.06,"2018-06-28T09:31:19",9.9999999999999978E-2,-1.7307692307692288E-2]
[6,28,2018,9,31,29,0.09,0.09,"2018-06-28T09:31:29",9.0000000000000011E-2,-1.153846153846142E-3]
[6,28,2018,9,31,39,0.06,0.06,"2018-06-28T09:31:39",8.5000000000000006E-2,1.269230769230769E-2]
[6,28,2018,9,31,49,0.03,0.03,"2018-06-28T09:31:49",6.9999999999999993E-2,2.4230769230769226E-2]
[6,28,2018,9,31,59,0,0,"2018-06-28T09:31:59",5.4999999999999993E-2,3.4615384615384603E-2]
[6,28,2018,9,32,9,-0.03,-0.03,"2018-06-28T09:32:09",3.4999999999999996E-2,4.1538461538461538E-2]
[6,28,2018,9,32,19,-0.06,-0.06,"2018-06-28T09:32:19",1.4999999999999999E-2,{"$f":"AVERAGE(G376:G401)","v":4.6153846153846163E-2}]
[6,28,2018,9,32,29,-0.06,-0.06,"2018-06-28T09:32:29",-0.01,4.9615384615384624E-2]
[6,28,2018,9,32,39,-0.09,-0.09,"2018-06-28T09:32:39",-3.4999999999999996E-2,5.0769230769230782E-2]
[6,28,2018,9,32,49,-0.09,-0.09,"2018-06-28T09:32:49",-5.4999999999999993E-2,4.8461538461538459E-2]
[6,28,2018,9,32,59,-0.12,-0.12,"2018-06-28T09:32:59",-7.4999999999999997E-2,4.3846153846153854E-2]
[6,28,2018,9,33,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T09:33:09",-9.5000000000000015E-2,3.923076923076925E-2]
[6,28,2018,9,33,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T09:33:19",-0.11,3.2307692307692308E-2]
[6,28,2018,9,33,29,-0.12,-0.12,"2018-06-28T09:33:29",-0.12000000000000001,2.6538461538461549E-2]
[6,28,2018,9,33,39,-0.24,-0.24,"2018-06-28T09:33:39",-0.14499999999999999,1.3846153846153845E-2]
[6,28,2018,9,33,49,-0.24,-0.24,"2018-06-28T09:33:49",-0.17,1.1538461538461548E-3]
[6,28,2018,9,33,59,-0.24,-0.24,"2018-06-28T09:33:59",-0.19000000000000003,-1.269230769230769E-2]
[6,28,2018,9,34,9,-0.24,-0.24,"2018-06-28T09:34:09",-0.20499999999999999,-2.6538461538461535E-2]
[6,28,2018,9,34,19,-0.27,-0.27,"2018-06-28T09:34:19",-0.22500000000000001,-4.1538461538461552E-2]
[6,28,2018,9,34,29,-0.24,-0.24,"2018-06-28T09:34:29",-0.245,-5.5384615384615393E-2]
[6,28,2018,9,34,39,-0.27,-0.27,"2018-06-28T09:34:39",-0.25,-7.0384615384615393E-2]
[6,28,2018,9,34,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T09:34:49",-0.26,-8.7692307692307708E-2]
[6,28,2018,9,34,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T09:34:59",-0.27,-0.10269230769230769]
[6,28,2018,9,35,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T09:35:09",-0.28000000000000003,-0.11884615384615384]
[6,28,2018,9,35,19,-0.33,-0.33,"2018-06-28T09:35:19",-0.29000000000000004,-0.13499999999999998]
[6,28,2018,9,35,29,-0.33,-0.33,"2018-06-28T09:35:29",-0.30500000000000005,-0.15115384615384614]
[6,28,2018,9,35,39,-0.36,-0.36,"2018-06-28T09:35:39",-0.32000000000000006,-0.16730769230769232]
[6,28,2018,9,35,49,-0.36,-0.36,"2018-06-28T09:35:49",-0.33,-0.18461538461538465]
[6,28,2018,9,35,59,-0.36,-0.36,"2018-06-28T09:35:59",-0.34,-0.20076923076923084]
[6,28,2018,9,36,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:36:09",-0.35999999999999993,-0.21807692307692311]
[6,28,2018,9,36,19,-0.51,-0.51,"2018-06-28T09:36:19",-0.38999999999999996,-0.2376923076923077]
[6,28,2018,9,36,29,-0.51,-0.51,"2018-06-28T09:36:29",-0.41999999999999993,-0.25615384615384618]
[6,28,2018,9,36,39,-0.51,-0.51,"2018-06-28T09:36:39",-0.44500000000000001,-0.27346153846153848]
[6,28,2018,9,36,49,-0.54,-0.54,"2018-06-28T09:36:49",-0.47500000000000003,-0.29192307692307695]
[6,28,2018,9,36,59,-0.54,-0.54,"2018-06-28T09:36:59",-0.505,-0.3092307692307692]
[6,28,2018,9,37,9,-0.57000000000000006,-0.57000000000000006,"2018-06-28T09:37:09",-0.53000000000000014,-0.32769230769230767]
[6,28,2018,9,37,19,-0.57000000000000006,-0.57000000000000006,"2018-06-28T09:37:19",-0.54,-0.34500000000000003]
[6,28,2018,9,37,29,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:37:29",-0.55500000000000005,-0.36230769230769222]
[6,28,2018,9,37,39,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:37:39",-0.57000000000000006,-0.37961538461538458]
[6,28,2018,9,37,49,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:37:49",-0.58000000000000007,-0.39807692307692299]
[6,28,2018,9,37,59,-0.63,-0.63,"2018-06-28T09:37:59",-0.59500000000000008,-0.41307692307692306]
[6,28,2018,9,38,9,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:38:09",-0.6,-0.42692307692307691]
[6,28,2018,9,38,19,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:38:19",-0.60500000000000009,-0.44076923076923075]
[6,28,2018,9,38,29,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:38:29",-0.60500000000000009,-0.45461538461538453]
[6,28,2018,9,38,39,-0.63,-0.63,"2018-06-28T09:38:39",-0.61,-0.46846153846153843]
[6,28,2018,9,38,49,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:38:49",-0.61,-0.48230769230769227]
[6,28,2018,9,38,59,-0.63,-0.63,{"$f":"DATE(C441,A441,B441)+TIME(D441,E441,F441)","v":"2018-06-28T09:38:59"},-0.61,-0.49615384615384617]
[6,28,2018,9,39,9,-0.63,-0.63,"2018-06-28T09:39:09",-0.61499999999999999,-0.50884615384615384]
[6,28,2018,9,39,19,-0.63,-0.63,"2018-06-28T09:39:19",-0.62,-0.52153846153846162]
[6,28,2018,9,39,29,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:39:29",-0.62,-0.53307692307692311]
[6,28,2018,9,39,39,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:39:39",{"$f":"AVERAGE(G440:G445)","v":-0.61499999999999999},-0.54346153846153844]
[6,28,2018,9,39,49,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:39:49",-0.6150000000000001,-0.55384615384615388]
[6,28,2018,9,39,59,-0.63,-0.63,"2018-06-28T09:39:59",-0.61499999999999999,-0.56423076923076931]
[6,28,2018,9,40,9,-0.63,-0.63,"2018-06-28T09:40:09",-0.61499999999999999,-0.57461538461538475]
[6,28,2018,9,40,19,-0.63,-0.63,"2018-06-28T09:40:19",-0.61499999999999999,-0.58500000000000019]
[6,28,2018,9,40,29,-0.63,-0.63,"2018-06-28T09:40:29",-0.62,-0.59307692307692328]
[6,28,2018,9,40,39,-0.66,-0.66,"2018-06-28T09:40:39",-0.63,-0.59884615384615403]
[6,28,2018,9,40,49,-0.66,-0.66,"2018-06-28T09:40:49",-0.64,-0.60461538461538489]
[6,28,2018,9,40,59,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:40:59",-0.63500000000000012,-0.60807692307692318]
[6,28,2018,9,41,9,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:41:09",-0.63,-0.61038461538461553]
[6,28,2018,9,41,19,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:41:19",-0.62500000000000011,-0.61269230769230776]
[6,28,2018,9,41,29,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:41:29",-0.62000000000000011,-0.61384615384615393]
[6,28,2018,9,41,39,-0.57000000000000006,-0.57000000000000006,"2018-06-28T09:41:39",-0.60500000000000009,-0.61384615384615393]
[6,28,2018,9,41,49,-0.57000000000000006,-0.57000000000000006,"2018-06-28T09:41:49",-0.59000000000000019,-0.61269230769230787]
[6,28,2018,9,41,59,-0.57000000000000006,-0.57000000000000006,"2018-06-28T09:41:59",-0.58500000000000008,-0.61153846153846159]
[6,28,2018,9,42,9,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:42:09",-0.58500000000000008,-0.61153846153846159]
[6,28,2018,9,42,19,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:42:19",-0.58500000000000008,-0.6103846153846153]
[6,28,2018,9,42,29,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:42:29",-0.58500000000000008,-0.6103846153846153]
[6,28,2018,9,42,39,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:42:39",-0.59000000000000008,-0.6103846153846153]
[6,28,2018,9,42,49,-0.60000000000000009,-0.60000000000000009,"2018-06-28T09:42:49",-0.59500000000000008,-0.6103846153846153]
[6,28,2018,9,42,59,-0.57000000000000006,-0.57000000000000006,"2018-06-28T09:42:59",-0.59500000000000008,{"$f":"AVERAGE(G440:G465)","v":-0.60807692307692296}]
[6,28,2018,9,43,9,-0.57000000000000006,-0.57000000000000006,"2018-06-28T09:43:09",-0.59000000000000019,-0.6069230769230769]
[6,28,2018,9,43,19,-0.57000000000000006,-0.57000000000000006,"2018-06-28T09:43:19",-0.58500000000000008,-0.60461538461538455]
[6,28,2018,9,43,29,-0.54,-0.54,"2018-06-28T09:43:29",-0.57500000000000007,-0.60115384615384615]
[6,28,2018,9,43,39,-0.54,-0.54,"2018-06-28T09:43:39",-0.56500000000000006,-0.59769230769230763]
[6,28,2018,9,43,49,-0.51,-0.51,"2018-06-28T09:43:49",-0.54999999999999993,-0.59423076923076912]
[6,28,2018,9,43,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:43:59",-0.52500000000000002,-0.5873076923076922]
[6,28,2018,9,44,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:44:09",-0.5,-0.58038461538461528]
[6,28,2018,9,44,19,-0.36,-0.36,"2018-06-28T09:44:19",-0.46500000000000002,-0.56999999999999995]
[6,28,2018,9,44,29,-0.36,-0.36,"2018-06-28T09:44:29",-0.435,-0.55961538461538463]
[6,28,2018,9,44,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T09:44:39",-0.39500000000000002,-0.54692307692307696]
[6,28,2018,9,44,49,-0.27,-0.27,"2018-06-28T09:44:49",-0.35499999999999998,-0.533076923076923]
[6,28,2018,9,44,59,-0.27,-0.27,"2018-06-28T09:44:59",-0.33,-0.51807692307692299]
[6,28,2018,9,45,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T09:45:09",-0.29499999999999998,-0.50076923076923063]
[6,28,2018,9,45,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T09:45:19",-0.26,-0.4834615384615385]
[6,28,2018,9,45,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T09:45:29",-0.22500000000000001,-0.46615384615384614]
[6,28,2018,9,45,39,-0.12,-0.12,"2018-06-28T09:45:39",-0.19499999999999998,-0.44769230769230772]
[6,28,2018,9,45,49,0.03,0.03,"2018-06-28T09:45:49",-0.14500000000000002,-0.4234615384615385]
[6,28,2018,9,45,59,0.03,0.03,"2018-06-28T09:45:59",-9.4999999999999987E-2,-0.40038461538461545]
[6,28,2018,9,46,9,0,0,"2018-06-28T09:46:09",-0.06,-0.37846153846153852]
[6,28,2018,9,46,19,0,0,"2018-06-28T09:46:19",-3.5000000000000003E-2,-0.35653846153846164]
[6,28,2018,9,46,29,0.03,0.03,"2018-06-28T09:46:29",-5.0000000000000001E-3,-0.33230769230769247]
[6,28,2018,9,46,39,0,0,"2018-06-28T09:46:39",1.4999999999999999E-2,-0.30923076923076925]
[6,28,2018,9,46,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T09:46:49",-1.5000000000000005E-2,-0.29192307692307695]
[6,28,2018,9,46,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T09:46:59",-4.5000000000000005E-2,-0.27461538461538465]
[6,28,2018,9,47,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T09:47:09",-7.0000000000000007E-2,-0.25730769230769235]
[6,28,2018,9,47,19,-0.12,-0.12,"2018-06-28T09:47:19",-9.0000000000000011E-2,-0.24000000000000002]
[6,28,2018,9,47,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T09:47:29",-0.12000000000000001,-0.22384615384615386]
[6,28,2018,9,47,39,-0.18,-0.18,"2018-06-28T09:47:39",-0.15000000000000002,-0.2088461538461539]
[6,28,2018,9,47,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T09:47:49",-0.15,-0.19384615384615389]
[6,28,2018,9,47,59,-0.18,-0.18,"2018-06-28T09:47:59",-0.15500000000000003,-0.18000000000000002]
[6,28,2018,9,48,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T09:48:09",-0.155,-0.16615384615384615]
[6,28,2018,9,48,19,-0.24,-0.24,"2018-06-28T09:48:19",-0.17500000000000002,-0.15923076923076926]
[6,28,2018,9,48,29,-0.24,-0.24,"2018-06-28T09:48:29",-0.19000000000000003,-0.15230769230769234]
[6,28,2018,9,48,39,-0.27,-0.27,"2018-06-28T09:48:39",-0.20499999999999999,-0.14884615384615388]
[6,28,2018,9,48,49,-0.27,-0.27,"2018-06-28T09:48:49",-0.22500000000000001,-0.14538461538461539]
[6,28,2018,9,48,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T09:48:59",-0.245,-0.14538461538461539]
[6,28,2018,9,49,9,-0.33,-0.33,"2018-06-28T09:49:09",-0.27500000000000002,-0.14769230769230773]
[6,28,2018,9,49,19,-0.33,-0.33,"2018-06-28T09:49:19",-0.29000000000000004,-0.15000000000000002]
[6,28,2018,9,49,29,-0.33,-0.33,"2018-06-28T09:49:29",-0.30500000000000005,-0.15461538461538463]
[6,28,2018,9,49,39,-0.33,-0.33,{"$f":"DATE(C505,A505,B505)+TIME(D505,E505,F505)","v":"2018-06-28T09:49:39"},-0.31500000000000006,-0.16153846153846155]
[6,28,2018,9,49,49,-0.36,-0.36,"2018-06-28T09:49:49",-0.33000000000000007,-0.16961538461538467]
[6,28,2018,9,49,59,-0.36,-0.36,"2018-06-28T09:49:59",-0.34,-0.1788461538461539]
[6,28,2018,9,50,9,-0.36,-0.36,"2018-06-28T09:50:09",-0.34499999999999997,-0.19384615384615392]
[6,28,2018,9,50,19,-0.36,-0.36,"2018-06-28T09:50:19",{"$f":"AVERAGE(G504:G509)","v":-0.34999999999999992},-0.2088461538461539]
[6,28,2018,9,50,29,-0.36,-0.36,"2018-06-28T09:50:29",-0.35499999999999993,-0.22269230769230777]
[6,28,2018,9,50,39,-0.39,-0.39,"2018-06-28T09:50:39",-0.36499999999999999,-0.23769230769230776]
[6,28,2018,9,50,49,-0.39,-0.39,"2018-06-28T09:50:49",-0.37000000000000005,-0.25384615384615389]
[6,28,2018,9,50,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:50:59",-0.38000000000000006,-0.27000000000000007]
[6,28,2018,9,51,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:51:09",-0.38999999999999996,-0.2803846153846154]
[6,28,2018,9,51,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:51:19",-0.40499999999999997,-0.29192307692307701]
[6,28,2018,9,51,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:51:29",-0.4200000000000001,-0.3034615384615385]
[6,28,2018,9,51,39,-0.51,-0.51,"2018-06-28T09:51:39",-0.43999999999999995,-0.31846153846153852]
[6,28,2018,9,51,49,-0.48,-0.48,"2018-06-28T09:51:49",-0.45500000000000002,-0.33115384615384619]
[6,28,2018,9,51,59,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:51:59",-0.45999999999999996,-0.34153846153846151]
[6,28,2018,9,52,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:52:09",-0.46500000000000002,-0.35307692307692301]
[6,28,2018,9,52,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:52:19",-0.46500000000000002,-0.36346153846153839]
[6,28,2018,9,52,29,-0.39,-0.39,"2018-06-28T09:52:29",-0.45500000000000002,-0.3726923076923076]
[6,28,2018,9,52,39,-0.36,-0.36,"2018-06-28T09:52:39",-0.42999999999999994,-0.37730769230769218]
[6,28,2018,9,52,49,-0.33,-0.33,"2018-06-28T09:52:49",-0.40499999999999997,-0.38076923076923069]
[6,28,2018,9,52,59,-0.27,-0.27,"2018-06-28T09:52:59",-0.375,-0.38076923076923069]
[6,28,2018,9,53,9,-0.27,-0.27,"2018-06-28T09:53:09",-0.34500000000000003,-0.38076923076923069]
[6,28,2018,9,53,19,-0.24,-0.24,"2018-06-28T09:53:19",-0.31,-0.37846153846153846]
[6,28,2018,9,53,29,-0.24,-0.24,"2018-06-28T09:53:29",-0.28499999999999998,-0.375]
[6,28,2018,9,53,39,-0.24,-0.24,"2018-06-28T09:53:39",-0.26500000000000001,{"$f":"AVERAGE(G504:G529)","v":-0.37153846153846154}]
[6,28,2018,9,53,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T09:53:49",-0.245,-0.36692307692307691]
[6,28,2018,9,53,59,-0.24,-0.24,"2018-06-28T09:53:59",-0.24,-0.36346153846153856]
[6,28,2018,9,54,9,-0.27,-0.27,"2018-06-28T09:54:09",-0.24,-0.36000000000000004]
[6,28,2018,9,54,19,-0.33,-0.33,"2018-06-28T09:54:19",-0.255,-0.35884615384615393]
[6,28,2018,9,54,29,-0.33,-0.33,"2018-06-28T09:54:29",-0.27,-0.35769230769230781]
[6,28,2018,9,54,39,-0.33,-0.33,"2018-06-28T09:54:39",-0.28500000000000003,-0.35653846153846153]
[6,28,2018,9,54,49,-0.36,-0.36,"2018-06-28T09:54:49",-0.31000000000000005,-0.35653846153846158]
[6,28,2018,9,54,59,-0.36,-0.36,"2018-06-28T09:54:59",-0.33,-0.35538461538461541]
[6,28,2018,9,55,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:55:09",-0.36000000000000004,-0.35769230769230764]
[6,28,2018,9,55,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T09:55:19",-0.37999999999999995,-0.35884615384615376]
[6,28,2018,9,55,29,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:55:29",-0.39499999999999996,-0.35884615384615387]
[6,28,2018,9,55,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T09:55:39",-0.41,-0.3576923076923077]
[6,28,2018,9,55,49,-0.36,-0.36,"2018-06-28T09:55:49",-0.40999999999999992,-0.35423076923076924]
[6,28,2018,9,55,59,-0.36,-0.36,"2018-06-28T09:55:59",-0.40999999999999992,-0.34846153846153849]
[6,28,2018,9,56,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T09:56:09",-0.38499999999999995,-0.34153846153846157]
[6,28,2018,9,56,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T09:56:19",-0.36000000000000004,-0.33576923076923088]
[6,28,2018,9,56,29,-0.27,-0.27,"2018-06-28T09:56:29",-0.33500000000000002,-0.32884615384615395]
[6,28,2018,9,56,39,-0.27,-0.27,"2018-06-28T09:56:39",-0.31,-0.32192307692307698]
[6,28,2018,9,56,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T09:56:49",-0.28499999999999998,-0.31500000000000006]
[6,28,2018,9,56,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T09:56:59",-0.26,-0.30923076923076925]
[6,28,2018,9,57,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T09:57:09",-0.23500000000000001,-0.30230769230769228]
[6,28,2018,9,57,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T09:57:19",-0.20999999999999996,-0.2976923076923077]
[6,28,2018,9,57,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T09:57:29",-0.19000000000000003,-0.29307692307692312]
[6,28,2018,9,57,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T09:57:39",-0.17,-0.28961538461538466]
[6,28,2018,9,57,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T09:57:49",-0.17,-0.28846153846153849]
[6,28,2018,9,57,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T09:57:59",-0.16,-0.28500000000000003]
[6,28,2018,9,58,9,-0.18,-0.18,"2018-06-28T09:58:09",-0.16500000000000004,-0.28384615384615391]
[6,28,2018,9,58,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T09:58:19",-0.17500000000000002,-0.28269230769230774]
[6,28,2018,9,58,29,-0.24,-0.24,"2018-06-28T09:58:29",-0.18999999999999997,-0.28153846153846157]
[6,28,2018,9,58,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T09:58:39",-0.19999999999999998,-0.27692307692307694]
[6,28,2018,9,58,49,-0.33,-0.33,"2018-06-28T09:58:49",-0.22,-0.27692307692307694]
[6,28,2018,9,58,59,-0.33,-0.33,"2018-06-28T09:58:59",-0.25000000000000006,-0.27692307692307694]
[6,28,2018,9,59,9,-0.36,-0.36,"2018-06-28T09:59:09",-0.28000000000000003,-0.27692307692307694]
[6,28,2018,9,59,19,-0.36,-0.36,"2018-06-28T09:59:19",-0.30499999999999999,-0.27692307692307699]
[6,28,2018,9,59,29,-0.36,-0.36,"2018-06-28T09:59:29",-0.32499999999999996,-0.27346153846153853]
[6,28,2018,9,59,39,-0.39,-0.39,"2018-06-28T09:59:39",-0.35499999999999998,-0.27115384615384619]
[6,28,2018,9,59,49,-0.27,-0.27,"2018-06-28T09:59:49",-0.34499999999999997,-0.26538461538461539]
[6,28,2018,9,59,59,-0.27,-0.27,"2018-06-28T09:59:59",-0.33500000000000002,-0.25961538461538464]
[6,28,2018,10,0,9,-0.24,-0.24,"2018-06-28T10:00:09",-0.315,-0.255]
[6,28,2018,10,0,19,-0.27,-0.27,{"$f":"DATE(C569,A569,B569)+TIME(D569,E569,F569)","v":"2018-06-28T10:00:19"},-0.3,-0.25153846153846149]
[6,28,2018,10,0,29,-0.27,-0.27,"2018-06-28T10:00:29",-0.28499999999999998,-0.25038461538461537]
[6,28,2018,10,0,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:00:39",-0.27,-0.25038461538461532]
[6,28,2018,10,0,49,-0.27,-0.27,"2018-06-28T10:00:49",-0.27,-0.25038461538461537]
[6,28,2018,10,0,59,-0.27,-0.27,"2018-06-28T10:00:59",{"$f":"AVERAGE(G568:G573)","v":-0.27},-0.25038461538461532]
[6,28,2018,10,1,9,-0.27,-0.27,"2018-06-28T10:01:09",-0.27500000000000002,-0.25269230769230766]
[6,28,2018,10,1,19,-0.27,-0.27,"2018-06-28T10:01:19",-0.27500000000000002,-0.25499999999999989]
[6,28,2018,10,1,29,-0.33,-0.33,"2018-06-28T10:01:29",-0.28500000000000003,-0.26192307692307687]
[6,28,2018,10,1,39,-0.36,-0.36,"2018-06-28T10:01:39",-0.29499999999999998,-0.26999999999999996]
[6,28,2018,10,1,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:01:49",-0.3,-0.27576923076923071]
[6,28,2018,10,1,59,-0.33,-0.33,"2018-06-28T10:01:59",-0.31,-0.28269230769230769]
[6,28,2018,10,2,9,-0.27,-0.27,"2018-06-28T10:02:09",-0.31000000000000005,-0.28499999999999992]
[6,28,2018,10,2,19,-0.24,-0.24,"2018-06-28T10:02:19",-0.30499999999999999,-0.28846153846153838]
[6,28,2018,10,2,29,-0.24,-0.24,"2018-06-28T10:02:29",-0.28999999999999998,-0.29076923076923072]
[6,28,2018,10,2,39,-0.24,-0.24,"2018-06-28T10:02:39",-0.27,-0.2919230769230769]
[6,28,2018,10,2,49,-0.24,-0.24,"2018-06-28T10:02:49",-0.26,-0.2919230769230769]
[6,28,2018,10,2,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:02:59",-0.24,-0.2919230769230769]
[6,28,2018,10,3,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T10:03:09",-0.21999999999999997,-0.28500000000000003]
[6,28,2018,10,3,19,-0.12,-0.12,"2018-06-28T10:03:19",-0.20000000000000004,-0.27692307692307694]
[6,28,2018,10,3,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T10:03:29",-0.18499999999999997,-0.2688461538461539]
[6,28,2018,10,3,39,-0.18,-0.18,"2018-06-28T10:03:39",-0.17500000000000002,-0.26192307692307704]
[6,28,2018,10,3,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:03:49",-0.17,-0.25615384615384618]
[6,28,2018,10,3,59,-0.27,-0.27,"2018-06-28T10:03:59",-0.18000000000000002,-0.25153846153846166]
[6,28,2018,10,4,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:04:09",-0.20499999999999999,-0.25269230769230772]
[6,28,2018,10,4,19,-0.33,-0.33,"2018-06-28T10:04:19",-0.24000000000000002,{"$f":"AVERAGE(G568:G593)","v":-0.25500000000000006}]
[6,28,2018,10,4,29,-0.33,-0.33,"2018-06-28T10:04:29",-0.27,-0.25846153846153852]
[6,28,2018,10,4,39,-0.33,-0.33,"2018-06-28T10:04:39",-0.29500000000000004,-0.26076923076923086]
[6,28,2018,10,4,49,-0.33,-0.33,"2018-06-28T10:04:49",-0.31500000000000006,-0.2630769230769231]
[6,28,2018,10,4,59,-0.36,-0.36,"2018-06-28T10:04:59",-0.33000000000000007,-0.26538461538461539]
[6,28,2018,10,5,9,-0.39,-0.39,"2018-06-28T10:05:09",-0.34500000000000003,-0.27]
[6,28,2018,10,5,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:05:19",-0.36000000000000004,-0.27576923076923082]
[6,28,2018,10,5,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T10:05:29",-0.38000000000000006,-0.28269230769230774]
[6,28,2018,10,5,39,-0.48,-0.48,"2018-06-28T10:05:39",-0.40499999999999997,-0.29076923076923078]
[6,28,2018,10,5,49,-0.51,-0.51,"2018-06-28T10:05:49",-0.43499999999999989,-0.2976923076923077]
[6,28,2018,10,5,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:05:59",-0.44500000000000001,-0.30000000000000004]
[6,28,2018,10,6,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T10:06:09",-0.45500000000000007,-0.30576923076923079]
[6,28,2018,10,6,19,-0.48,-0.48,"2018-06-28T10:06:19",-0.46499999999999991,-0.31153846153846154]
[6,28,2018,10,6,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T10:06:29",-0.46500000000000002,-0.31846153846153846]
[6,28,2018,10,6,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:06:39",-0.4549999999999999,-0.32538461538461533]
[6,28,2018,10,6,49,-0.36,-0.36,"2018-06-28T10:06:49",-0.43,-0.33]
[6,28,2018,10,6,59,-0.33,-0.33,"2018-06-28T10:06:59",-0.41499999999999998,-0.33346153846153848]
[6,28,2018,10,7,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:07:09",-0.38999999999999996,-0.33576923076923076]
[6,28,2018,10,7,19,-0.33,-0.33,"2018-06-28T10:07:19",-0.36499999999999999,-0.34038461538461545]
[6,28,2018,10,7,29,-0.39,-0.39,"2018-06-28T10:07:29",-0.35500000000000004,-0.34961538461538466]
[6,28,2018,10,7,39,-0.39,-0.39,"2018-06-28T10:07:39",-0.35000000000000003,-0.36000000000000004]
[6,28,2018,10,7,49,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:07:49",-0.36000000000000004,-0.37038461538461548]
[6,28,2018,10,7,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:07:59",-0.375,-0.37961538461538458]
[6,28,2018,10,8,9,-0.39,-0.39,"2018-06-28T10:08:09",-0.38999999999999996,-0.38653846153846161]
[6,28,2018,10,8,19,-0.39,-0.39,"2018-06-28T10:08:19",-0.40000000000000008,-0.39115384615384624]
[6,28,2018,10,8,29,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:08:29",-0.40500000000000003,-0.39576923076923087]
[6,28,2018,10,8,39,-0.39,-0.39,"2018-06-28T10:08:39",-0.40500000000000003,-0.39807692307692322]
[6,28,2018,10,8,49,-0.33,-0.33,"2018-06-28T10:08:49",-0.39000000000000007,-0.39807692307692322]
[6,28,2018,10,8,59,-0.36,-0.36,"2018-06-28T10:08:59",-0.38000000000000006,-0.39923076923076928]
[6,28,2018,10,9,9,-0.39,-0.39,"2018-06-28T10:09:09",-0.38000000000000006,-0.40153846153846151]
[6,28,2018,10,9,19,-0.39,-0.39,"2018-06-28T10:09:19",-0.38000000000000006,-0.40269230769230774]
[6,28,2018,10,9,29,-0.39,-0.39,"2018-06-28T10:09:29",-0.37500000000000006,-0.40269230769230774]
[6,28,2018,10,9,39,-0.44999999999999996,-0.44999999999999996,"2018-06-28T10:09:39",-0.38500000000000006,-0.4038461538461538]
[6,28,2018,10,9,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T10:09:49",-0.40500000000000003,-0.4038461538461538]
[6,28,2018,10,9,59,-0.44999999999999996,-0.44999999999999996,"2018-06-28T10:09:59",-0.41999999999999993,-0.40269230769230757]
[6,28,2018,10,10,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:10:09",-0.42499999999999999,-0.39923076923076911]
[6,28,2018,10,10,19,-0.51,-0.51,"2018-06-28T10:10:19",-0.44500000000000001,-0.40269230769230757]
[6,28,2018,10,10,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T10:10:29",-0.45500000000000007,-0.40269230769230752]
[6,28,2018,10,10,39,-0.60000000000000009,-0.60000000000000009,"2018-06-28T10:10:39",-0.48,-0.40730769230769215]
[6,28,2018,10,10,49,-0.54,-0.54,"2018-06-28T10:10:49",-0.49499999999999994,-0.41076923076923078]
[6,28,2018,10,10,59,-0.57000000000000006,-0.57000000000000006,{"$f":"DATE(C633,A633,B633)+TIME(D633,E633,F633)","v":"2018-06-28T10:10:59"},-0.51500000000000001,-0.41653846153846147]
[6,28,2018,10,11,9,-0.60000000000000009,-0.60000000000000009,"2018-06-28T10:11:09",-0.54500000000000004,-0.42576923076923073]
[6,28,2018,10,11,19,-0.57000000000000006,-0.57000000000000006,"2018-06-28T10:11:19",-0.55500000000000005,-0.435]
[6,28,2018,10,11,29,-0.57000000000000006,-0.57000000000000006,"2018-06-28T10:11:29",-0.57500000000000018,-0.44538461538461538]
[6,28,2018,10,11,39,-0.57000000000000006,-0.57000000000000006,"2018-06-28T10:11:39",{"$f":"AVERAGE(G632:G637)","v":-0.57000000000000017},-0.4546153846153847]
[6,28,2018,10,11,49,-0.48,-0.48,"2018-06-28T10:11:49",-0.56000000000000016,-0.45807692307692316]
[6,28,2018,10,11,59,-0.44999999999999996,-0.44999999999999996,"2018-06-28T10:11:59",-0.54,-0.46038461538461539]
[6,28,2018,10,12,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T10:12:09",-0.51500000000000012,-0.46153846153846156]
[6,28,2018,10,12,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:12:19",-0.49000000000000005,-0.46153846153846162]
[6,28,2018,10,12,29,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:12:29",-0.46500000000000002,-0.46269230769230774]
[6,28,2018,10,12,39,-0.36,-0.36,"2018-06-28T10:12:39",-0.42999999999999994,-0.46153846153846156]
[6,28,2018,10,12,49,-0.36,-0.36,"2018-06-28T10:12:49",-0.40999999999999992,-0.45923076923076922]
[6,28,2018,10,12,59,-0.36,-0.36,"2018-06-28T10:12:59",-0.39499999999999996,-0.4580769230769231]
[6,28,2018,10,13,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:13:09",-0.36999999999999994,-0.45692307692307688]
[6,28,2018,10,13,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:13:19",-0.35000000000000003,-0.45461538461538464]
[6,28,2018,10,13,29,-0.33,-0.33,"2018-06-28T10:13:29",-0.33500000000000002,-0.4523076923076923]
[6,28,2018,10,13,39,-0.27,-0.27,"2018-06-28T10:13:39",-0.32,-0.44769230769230767]
[6,28,2018,10,13,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:13:49",-0.31,-0.44423076923076932]
[6,28,2018,10,13,59,-0.27,-0.27,"2018-06-28T10:13:59",-0.29500000000000004,-0.43730769230769234]
[6,28,2018,10,14,9,-0.33,-0.33,"2018-06-28T10:14:09",-0.30000000000000004,-0.43269230769230776]
[6,28,2018,10,14,19,-0.27,-0.27,"2018-06-28T10:14:19",-0.29500000000000004,-0.42576923076923084]
[6,28,2018,10,14,29,-0.27,-0.27,"2018-06-28T10:14:29",-0.28500000000000003,-0.42000000000000004]
[6,28,2018,10,14,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:14:39",-0.29000000000000004,-0.411923076923077]
[6,28,2018,10,14,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:14:49",-0.29000000000000004,-0.40615384615384625]
[6,28,2018,10,14,59,-0.27,-0.27,"2018-06-28T10:14:59",-0.29000000000000004,{"$f":"AVERAGE(G632:G657)","v":-0.39346153846153853}]
[6,28,2018,10,15,9,-0.24,-0.24,"2018-06-28T10:15:09",-0.27500000000000002,-0.38192307692307698]
[6,28,2018,10,15,19,-0.24,-0.24,"2018-06-28T10:15:19",-0.27,-0.36923076923076931]
[6,28,2018,10,15,29,-0.24,-0.24,"2018-06-28T10:15:29",-0.26500000000000001,-0.35538461538461541]
[6,28,2018,10,15,39,-0.24,-0.24,"2018-06-28T10:15:39",-0.255,-0.34269230769230768]
[6,28,2018,10,15,49,-0.24,-0.24,"2018-06-28T10:15:49",-0.245,-0.33]
[6,28,2018,10,15,59,-0.24,-0.24,"2018-06-28T10:15:59",-0.24,-0.31730769230769229]
[6,28,2018,10,16,9,-0.24,-0.24,"2018-06-28T10:16:09",-0.24,-0.30807692307692308]
[6,28,2018,10,16,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:16:19",-0.25,-0.30230769230769233]
[6,28,2018,10,16,29,-0.27,-0.27,"2018-06-28T10:16:29",-0.255,-0.29538461538461536]
[6,28,2018,10,16,39,-0.27,-0.27,"2018-06-28T10:16:39",-0.26,-0.28961538461538466]
[6,28,2018,10,16,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:16:49",-0.255,-0.28153846153846157]
[6,28,2018,10,16,59,-0.24,-0.24,"2018-06-28T10:16:59",-0.255,-0.27692307692307699]
[6,28,2018,10,17,9,-0.27,-0.27,"2018-06-28T10:17:09",-0.26,-0.27346153846153853]
[6,28,2018,10,17,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:17:19",-0.26,-0.27115384615384619]
[6,28,2018,10,17,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:17:29",-0.26500000000000001,-0.27115384615384619]
[6,28,2018,10,17,39,-0.33,-0.33,"2018-06-28T10:17:39",-0.27500000000000002,-0.27230769230769231]
[6,28,2018,10,17,49,-0.33,-0.33,"2018-06-28T10:17:49",-0.29500000000000004,-0.27230769230769236]
[6,28,2018,10,17,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:17:59",-0.30500000000000005,-0.27346153846153848]
[6,28,2018,10,18,9,-0.33,-0.33,"2018-06-28T10:18:09",-0.31500000000000006,-0.27461538461538465]
[6,28,2018,10,18,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:18:19",-0.31500000000000006,-0.27576923076923077]
[6,28,2018,10,18,29,-0.33,-0.33,"2018-06-28T10:18:29",-0.32,-0.27576923076923077]
[6,28,2018,10,18,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:18:39",-0.31500000000000006,-0.27692307692307694]
[6,28,2018,10,18,49,-0.33,-0.33,"2018-06-28T10:18:49",-0.31500000000000006,-0.27923076923076928]
[6,28,2018,10,18,59,-0.33,-0.33,"2018-06-28T10:18:59",-0.32000000000000006,-0.2803846153846154]
[6,28,2018,10,19,9,-0.33,-0.33,"2018-06-28T10:19:09",-0.32000000000000006,-0.28153846153846157]
[6,28,2018,10,19,19,-0.36,-0.36,"2018-06-28T10:19:19",-0.33000000000000007,-0.28500000000000003]
[6,28,2018,10,19,29,-0.36,-0.36,"2018-06-28T10:19:29",-0.33500000000000002,-0.28961538461538461]
[6,28,2018,10,19,39,-0.39,-0.39,"2018-06-28T10:19:39",-0.35000000000000003,-0.29538461538461541]
[6,28,2018,10,19,49,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:19:49",-0.36499999999999999,-0.30230769230769233]
[6,28,2018,10,19,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:19:59",-0.37999999999999995,-0.30923076923076925]
[6,28,2018,10,20,9,-0.39,-0.39,"2018-06-28T10:20:09",-0.38999999999999996,-0.315]
[6,28,2018,10,20,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:20:19",-0.39999999999999997,-0.32192307692307698]
[6,28,2018,10,20,29,-0.39,-0.39,"2018-06-28T10:20:29",-0.40500000000000003,-0.32769230769230773]
[6,28,2018,10,20,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:20:39",-0.41,-0.3323076923076923]
[6,28,2018,10,20,49,-0.36,-0.36,"2018-06-28T10:20:49",-0.39999999999999997,-0.33576923076923071]
[6,28,2018,10,20,59,-0.39,-0.39,"2018-06-28T10:20:59",-0.39500000000000002,-0.3403846153846154]
[6,28,2018,10,21,9,-0.39,-0.39,"2018-06-28T10:21:09",-0.39500000000000002,-0.34730769230769237]
[6,28,2018,10,21,19,-0.36,-0.36,"2018-06-28T10:21:19",-0.38500000000000001,-0.35192307692307695]
[6,28,2018,10,21,29,-0.36,-0.36,"2018-06-28T10:21:29",-0.37999999999999995,-0.35538461538461541]
[6,28,2018,10,21,39,-0.39,-0.39,{"$f":"DATE(C697,A697,B697)+TIME(D697,E697,F697)","v":"2018-06-28T10:21:39"},-0.375,-0.35884615384615376]
[6,28,2018,10,21,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T10:21:49",-0.38999999999999996,-0.36461538461538456]
[6,28,2018,10,21,59,-0.39,-0.39,"2018-06-28T10:21:59",-0.38999999999999996,-0.36692307692307691]
[6,28,2018,10,22,9,-0.36,-0.36,"2018-06-28T10:22:09",-0.38499999999999995,-0.36807692307692302]
[6,28,2018,10,22,19,-0.36,-0.36,"2018-06-28T10:22:19",{"$f":"AVERAGE(G696:G701)","v":-0.38499999999999995},-0.37038461538461537]
[6,28,2018,10,22,29,-0.36,-0.36,"2018-06-28T10:22:29",-0.38499999999999995,-0.37153846153846148]
[6,28,2018,10,22,39,-0.33,-0.33,"2018-06-28T10:22:39",-0.375,-0.37269230769230766]
[6,28,2018,10,22,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:22:49",-0.34999999999999992,-0.37153846153846154]
[6,28,2018,10,22,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:22:59",-0.33500000000000002,-0.37153846153846154]
[6,28,2018,10,23,9,-0.27,-0.27,"2018-06-28T10:23:09",-0.32,-0.36923076923076931]
[6,28,2018,10,23,19,-0.27,-0.27,"2018-06-28T10:23:19",-0.30499999999999999,-0.36692307692307696]
[6,28,2018,10,23,29,-0.27,-0.27,"2018-06-28T10:23:29",-0.29000000000000004,-0.36461538461538462]
[6,28,2018,10,23,39,-0.27,-0.27,"2018-06-28T10:23:39",-0.28000000000000003,-0.36115384615384616]
[6,28,2018,10,23,49,-0.09,-0.09,"2018-06-28T10:23:49",-0.24500000000000002,-0.35076923076923072]
[6,28,2018,10,23,59,-0.12,-0.12,"2018-06-28T10:23:59",-0.215,-0.34038461538461529]
[6,28,2018,10,24,9,-0.06,-0.06,"2018-06-28T10:24:09",-0.18000000000000002,-0.3265384615384615]
[6,28,2018,10,24,19,-0.06,-0.06,"2018-06-28T10:24:19",-0.14500000000000002,-0.31269230769230766]
[6,28,2018,10,24,29,-0.06,-0.06,"2018-06-28T10:24:29",-0.11000000000000003,-0.29999999999999988]
[6,28,2018,10,24,39,-0.06,-0.06,"2018-06-28T10:24:39",-7.4999999999999997E-2,-0.28615384615384604]
[6,28,2018,10,24,49,-0.27,-0.27,"2018-06-28T10:24:49",-0.105,-0.28153846153846146]
[6,28,2018,10,24,59,-0.24,-0.24,"2018-06-28T10:24:59",-0.125,-0.27461538461538448]
[6,28,2018,10,25,9,-0.24,-0.24,"2018-06-28T10:25:09",-0.155,-0.26999999999999991]
[6,28,2018,10,25,19,-0.27,-0.27,"2018-06-28T10:25:19",-0.19000000000000003,-0.26538461538461527]
[6,28,2018,10,25,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:25:29",-0.23,-0.26192307692307676]
[6,28,2018,10,25,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:25:39",-0.27,{"$f":"AVERAGE(G696:G721)","v":-0.25961538461538453}]
[6,28,2018,10,25,49,-0.27,-0.27,"2018-06-28T10:25:49",-0.27,-0.25615384615384601]
[6,28,2018,10,25,59,-0.24,-0.24,"2018-06-28T10:25:59",-0.27,-0.25038461538461532]
[6,28,2018,10,26,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:26:09",-0.28000000000000003,-0.24461538461538457]
[6,28,2018,10,26,19,-0.27,-0.27,"2018-06-28T10:26:19",-0.28000000000000003,-0.24000000000000002]
[6,28,2018,10,26,29,-0.27,-0.27,"2018-06-28T10:26:29",-0.27500000000000002,-0.23653846153846156]
[6,28,2018,10,26,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:26:39",-0.27500000000000002,-0.23423076923076927]
[6,28,2018,10,26,49,-0.27,-0.27,"2018-06-28T10:26:49",-0.27500000000000002,-0.23076923076923084]
[6,28,2018,10,26,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:26:59",-0.28500000000000003,-0.22961538461538467]
[6,28,2018,10,27,9,-0.33,-0.33,"2018-06-28T10:27:09",-0.29000000000000004,-0.23076923076923081]
[6,28,2018,10,27,19,-0.33,-0.33,"2018-06-28T10:27:19",-0.30000000000000004,-0.23192307692307693]
[6,28,2018,10,27,29,-0.33,-0.33,"2018-06-28T10:27:29",-0.31000000000000005,-0.23423076923076919]
[6,28,2018,10,27,39,-0.36,-0.36,"2018-06-28T10:27:39",-0.32000000000000006,-0.23769230769230767]
[6,28,2018,10,27,49,-0.39,-0.39,"2018-06-28T10:27:49",-0.34000000000000008,-0.24230769230769231]
[6,28,2018,10,27,59,-0.36,-0.36,"2018-06-28T10:27:59",-0.35000000000000003,-0.2457692307692308]
[6,28,2018,10,28,9,-0.36,-0.36,"2018-06-28T10:28:09",-0.35499999999999998,-0.25615384615384618]
[6,28,2018,10,28,19,-0.36,-0.36,"2018-06-28T10:28:19",-0.35999999999999993,-0.26538461538461544]
[6,28,2018,10,28,29,-0.36,-0.36,"2018-06-28T10:28:29",-0.36499999999999994,-0.27692307692307699]
[6,28,2018,10,28,39,-0.36,-0.36,"2018-06-28T10:28:39",-0.36499999999999994,-0.28846153846153855]
[6,28,2018,10,28,49,-0.39,-0.39,"2018-06-28T10:28:49",-0.36499999999999999,-0.30115384615384622]
[6,28,2018,10,28,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:28:59",-0.375,-0.31500000000000006]
[6,28,2018,10,29,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:29:09",-0.38500000000000001,-0.32076923076923081]
[6,28,2018,10,29,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:29:19",-0.39499999999999996,-0.32769230769230784]
[6,28,2018,10,29,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T10:29:29",-0.41,-0.33576923076923088]
[6,28,2018,10,29,39,-0.48,-0.48,"2018-06-28T10:29:39",-0.42999999999999994,-0.34384615384615391]
[6,28,2018,10,29,49,-0.48,-0.48,"2018-06-28T10:29:49",-0.44500000000000006,-0.35076923076923089]
[6,28,2018,10,29,59,-0.51,-0.51,"2018-06-28T10:29:59",-0.45999999999999996,-0.35884615384615393]
[6,28,2018,10,30,9,-0.48,-0.48,"2018-06-28T10:30:09",-0.47,-0.36692307692307702]
[6,28,2018,10,30,19,-0.51,-0.51,"2018-06-28T10:30:19",-0.48500000000000004,-0.37730769230769234]
[6,28,2018,10,30,29,-0.57000000000000006,-0.57000000000000006,"2018-06-28T10:30:29",-0.505,-0.38769230769230778]
[6,28,2018,10,30,39,-0.51,-0.51,"2018-06-28T10:30:39",-0.5099999999999999,-0.39692307692307693]
[6,28,2018,10,30,49,-0.51,-0.51,"2018-06-28T10:30:49",-0.51500000000000001,-0.4061538461538462]
[6,28,2018,10,30,59,-0.54,-0.54,"2018-06-28T10:30:59",-0.52,-0.41538461538461541]
[6,28,2018,10,31,9,-0.51,-0.51,"2018-06-28T10:31:09",-0.52500000000000002,-0.42461538461538467]
[6,28,2018,10,31,19,-0.54,-0.54,"2018-06-28T10:31:19",-0.52999999999999992,-0.43384615384615388]
[6,28,2018,10,31,29,-0.51,-0.51,"2018-06-28T10:31:29",-0.52,-0.44076923076923075]
[6,28,2018,10,31,39,-0.44999999999999996,-0.44999999999999996,"2018-06-28T10:31:39",-0.51000000000000012,-0.44538461538461538]
[6,28,2018,10,31,49,-0.48,-0.48,"2018-06-28T10:31:49",-0.505,-0.45115384615384613]
[6,28,2018,10,31,59,-0.48,-0.48,"2018-06-28T10:31:59",-0.49499999999999994,-0.45576923076923076]
[6,28,2018,10,32,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T10:32:09",-0.48500000000000004,-0.45807692307692299]
[6,28,2018,10,32,19,-0.42000000000000004,-0.42000000000000004,{"$f":"DATE(C761,A761,B761)+TIME(D761,E761,F761)","v":"2018-06-28T10:32:19"},-0.46500000000000002,-0.46038461538461534]
[6,28,2018,10,32,29,-0.39,-0.39,"2018-06-28T10:32:29",-0.44500000000000001,-0.46153846153846156]
[6,28,2018,10,32,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:32:39",-0.44,-0.4638461538461538]
[6,28,2018,10,32,49,-0.36,-0.36,"2018-06-28T10:32:49",-0.42,-0.4638461538461538]
[6,28,2018,10,32,59,-0.36,-0.36,"2018-06-28T10:32:59",{"$f":"AVERAGE(G760:G765)","v":-0.39999999999999997},-0.46384615384615374]
[6,28,2018,10,33,9,-0.33,-0.33,"2018-06-28T10:33:09",-0.37999999999999995,-0.46153846153846156]
[6,28,2018,10,33,19,-0.33,-0.33,"2018-06-28T10:33:19",-0.36499999999999999,-0.45807692307692299]
[6,28,2018,10,33,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:33:29",-0.35000000000000009,-0.45346153846153842]
[6,28,2018,10,33,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:33:39",-0.33,-0.44884615384615384]
[6,28,2018,10,33,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T10:33:49",-0.34500000000000003,-0.44884615384615384]
[6,28,2018,10,33,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:33:59",-0.35500000000000004,-0.4465384615384615]
[6,28,2018,10,34,9,-0.39,-0.39,"2018-06-28T10:34:09",-0.36500000000000005,-0.44307692307692303]
[6,28,2018,10,34,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T10:34:19",-0.38000000000000006,-0.43961538461538463]
[6,28,2018,10,34,29,-0.39,-0.39,"2018-06-28T10:34:29",-0.39500000000000002,-0.43615384615384628]
[6,28,2018,10,34,39,-0.39,-0.39,"2018-06-28T10:34:39",-0.41000000000000009,-0.43153846153846165]
[6,28,2018,10,34,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:34:49",-0.37000000000000005,-0.41769230769230781]
[6,28,2018,10,34,59,-0.24,-0.24,"2018-06-28T10:34:59",-0.34,-0.40730769230769243]
[6,28,2018,10,35,9,-0.18,-0.18,"2018-06-28T10:35:09",-0.30499999999999999,-0.39461538461538476]
[6,28,2018,10,35,19,-0.18,-0.18,"2018-06-28T10:35:19",-0.26499999999999996,-0.38076923076923086]
[6,28,2018,10,35,29,-0.12,-0.12,"2018-06-28T10:35:29",-0.21999999999999997,-0.36576923076923085]
[6,28,2018,10,35,39,-0.09,-0.09,"2018-06-28T10:35:39",-0.17,-0.34846153846153843]
[6,28,2018,10,35,49,-0.27,-0.27,"2018-06-28T10:35:49",-0.18000000000000002,-0.33923076923076911]
[6,28,2018,10,35,59,-0.27,-0.27,"2018-06-28T10:35:59",-0.18499999999999997,-0.33230769230769219]
[6,28,2018,10,36,9,-0.24,-0.24,"2018-06-28T10:36:09",-0.19499999999999998,-0.32307692307692304]
[6,28,2018,10,36,19,-0.24,-0.24,"2018-06-28T10:36:19",-0.20499999999999999,{"$f":"AVERAGE(G760:G785)","v":-0.31384615384615377}]
[6,28,2018,10,36,29,-0.24,-0.24,"2018-06-28T10:36:29",-0.22499999999999998,-0.30576923076923074]
[6,28,2018,10,36,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:36:39",-0.26,-0.30115384615384611]
[6,28,2018,10,36,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T10:36:49",-0.24,-0.29192307692307695]
[6,28,2018,10,36,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T10:36:59",-0.21999999999999997,-0.28153846153846152]
[6,28,2018,10,37,9,-0.18,-0.18,"2018-06-28T10:37:09",-0.21,-0.27461538461538459]
[6,28,2018,10,37,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:37:19",-0.20499999999999999,-0.26884615384615385]
[6,28,2018,10,37,29,-0.24,-0.24,"2018-06-28T10:37:29",-0.20499999999999999,-0.26538461538461539]
[6,28,2018,10,37,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:37:39",-0.19000000000000003,-0.26076923076923086]
[6,28,2018,10,37,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:37:49",-0.19999999999999998,-0.25730769230769235]
[6,28,2018,10,37,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:37:59",-0.21,-0.25384615384615389]
[6,28,2018,10,38,9,-0.24,-0.24,"2018-06-28T10:38:09",-0.22,-0.24576923076923082]
[6,28,2018,10,38,19,-0.24,-0.24,"2018-06-28T10:38:19",-0.22500000000000001,-0.2388461538461539]
[6,28,2018,10,38,29,-0.27,-0.27,"2018-06-28T10:38:29",-0.23,-0.23423076923076921]
[6,28,2018,10,38,39,-0.27,-0.27,"2018-06-28T10:38:39",-0.24,-0.22846153846153852]
[6,28,2018,10,38,49,-0.27,-0.27,"2018-06-28T10:38:49",-0.25,-0.22384615384615378]
[6,28,2018,10,38,59,-0.24,-0.24,"2018-06-28T10:38:59",-0.255,-0.21807692307692308]
[6,28,2018,10,39,9,-0.27,-0.27,"2018-06-28T10:39:09",-0.26,-0.22038461538461535]
[6,28,2018,10,39,19,-0.27,-0.27,"2018-06-28T10:39:19",-0.26500000000000001,-0.22153846153846146]
[6,28,2018,10,39,29,-0.27,-0.27,"2018-06-28T10:39:29",-0.26500000000000001,-0.22499999999999992]
[6,28,2018,10,39,39,-0.24,-0.24,"2018-06-28T10:39:39",-0.26,-0.22730769230769224]
[6,28,2018,10,39,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:39:49",-0.25,-0.23076923076923073]
[6,28,2018,10,39,59,-0.24,-0.24,"2018-06-28T10:39:59",-0.25,-0.23653846153846153]
[6,28,2018,10,40,9,-0.27,-0.27,"2018-06-28T10:40:09",-0.25,-0.23653846153846156]
[6,28,2018,10,40,19,-0.27,-0.27,"2018-06-28T10:40:19",-0.25,-0.23653846153846148]
[6,28,2018,10,40,29,-0.33,-0.33,"2018-06-28T10:40:29",-0.26,-0.24000000000000002]
[6,28,2018,10,40,39,-0.24,-0.24,"2018-06-28T10:40:39",-0.26,-0.24000000000000002]
[6,28,2018,10,40,49,-0.24,-0.24,"2018-06-28T10:40:49",-0.26500000000000001,-0.24000000000000002]
[6,28,2018,10,40,59,-0.24,-0.24,"2018-06-28T10:40:59",-0.26500000000000001,-0.23769230769230767]
[6,28,2018,10,41,9,-0.24,-0.24,"2018-06-28T10:41:09",-0.26,-0.24115384615384622]
[6,28,2018,10,41,19,-0.27,-0.27,"2018-06-28T10:41:19",-0.26,-0.2457692307692308]
[6,28,2018,10,41,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:41:29",-0.255,-0.25038461538461543]
[6,28,2018,10,41,39,-0.27,-0.27,"2018-06-28T10:41:39",-0.26,-0.25269230769230772]
[6,28,2018,10,41,49,-0.27,-0.27,"2018-06-28T10:41:49",-0.26500000000000001,-0.25384615384615389]
[6,28,2018,10,41,59,-0.27,-0.27,"2018-06-28T10:41:59",-0.27,-0.25615384615384618]
[6,28,2018,10,42,9,-0.27,-0.27,"2018-06-28T10:42:09",-0.27500000000000002,-0.25846153846153846]
[6,28,2018,10,42,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:42:19",-0.28000000000000003,-0.26192307692307693]
[6,28,2018,10,42,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:42:29",-0.28000000000000003,-0.26423076923076921]
[6,28,2018,10,42,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:42:39",-0.28500000000000003,-0.2665384615384615]
[6,28,2018,10,42,49,-0.33,-0.33,"2018-06-28T10:42:49",-0.29500000000000004,-0.26884615384615385]
[6,28,2018,10,42,59,-0.33,-0.33,{"$f":"DATE(C825,A825,B825)+TIME(D825,E825,F825)","v":"2018-06-28T10:42:59"},-0.30500000000000005,-0.27115384615384613]
[6,28,2018,10,43,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:43:09",-0.31000000000000005,-0.27230769230769225]
[6,28,2018,10,43,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:43:19",-0.31000000000000005,-0.27461538461538459]
[6,28,2018,10,43,29,-0.27,-0.27,"2018-06-28T10:43:29",-0.30500000000000005,-0.27461538461538465]
[6,28,2018,10,43,39,-0.27,-0.27,"2018-06-28T10:43:39",{"$f":"AVERAGE(G824:G829)","v":-0.30000000000000004},-0.27461538461538465]
[6,28,2018,10,43,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:43:49",-0.29500000000000004,-0.27576923076923071]
[6,28,2018,10,43,59,-0.33,-0.33,"2018-06-28T10:43:59",-0.29500000000000004,-0.27923076923076917]
[6,28,2018,10,44,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:44:09",-0.29500000000000004,-0.28269230769230769]
[6,28,2018,10,44,19,-0.27,-0.27,"2018-06-28T10:44:19",-0.29000000000000004,-0.2838461538461538]
[6,28,2018,10,44,29,-0.27,-0.27,"2018-06-28T10:44:29",-0.29000000000000004,-0.28384615384615375]
[6,28,2018,10,44,39,-0.33,-0.33,"2018-06-28T10:44:39",-0.30000000000000004,-0.28615384615384609]
[6,28,2018,10,44,49,-0.33,-0.33,"2018-06-28T10:44:49",-0.30500000000000005,-0.28615384615384609]
[6,28,2018,10,44,59,-0.39,-0.39,"2018-06-28T10:44:59",-0.315,-0.29192307692307684]
[6,28,2018,10,45,9,-0.33,-0.33,"2018-06-28T10:45:09",-0.32000000000000006,-0.29538461538461525]
[6,28,2018,10,45,19,-0.36,-0.36,"2018-06-28T10:45:19",-0.33500000000000002,-0.29999999999999993]
[6,28,2018,10,45,29,-0.36,-0.36,"2018-06-28T10:45:29",-0.35000000000000003,-0.30461538461538457]
[6,28,2018,10,45,39,-0.36,-0.36,"2018-06-28T10:45:39",-0.35499999999999998,-0.30807692307692308]
[6,28,2018,10,45,49,-0.36,-0.36,"2018-06-28T10:45:49",-0.35999999999999993,-0.31038461538461537]
[6,28,2018,10,45,59,-0.36,-0.36,"2018-06-28T10:45:59",-0.35499999999999993,-0.31384615384615383]
[6,28,2018,10,46,9,-0.33,-0.33,"2018-06-28T10:46:09",-0.35499999999999998,-0.31615384615384617]
[6,28,2018,10,46,19,-0.27,-0.27,"2018-06-28T10:46:19",-0.34,-0.31615384615384617]
[6,28,2018,10,46,29,-0.24,-0.24,"2018-06-28T10:46:29",-0.32,-0.31500000000000006]
[6,28,2018,10,46,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:46:39",-0.29499999999999998,-0.31153846153846165]
[6,28,2018,10,46,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:46:49",-0.26999999999999996,-0.30807692307692314]
[6,28,2018,10,46,59,-0.27,-0.27,"2018-06-28T10:46:59",-0.255,{"$f":"AVERAGE(G824:G849)","v":-0.30692307692307702}]
[6,28,2018,10,47,9,-0.27,-0.27,"2018-06-28T10:47:09",-0.245,-0.30461538461538468]
[6,28,2018,10,47,19,-0.24,-0.24,"2018-06-28T10:47:19",-0.24000000000000002,-0.30115384615384622]
[6,28,2018,10,47,29,-0.24,-0.24,"2018-06-28T10:47:29",-0.24000000000000002,-0.29884615384615387]
[6,28,2018,10,47,39,-0.24,-0.24,"2018-06-28T10:47:39",-0.245,-0.29653846153846158]
[6,28,2018,10,47,49,-0.24,-0.24,"2018-06-28T10:47:49",-0.25,-0.29538461538461547]
[6,28,2018,10,47,59,-0.24,-0.24,"2018-06-28T10:47:59",-0.245,-0.29423076923076924]
[6,28,2018,10,48,9,-0.24,-0.24,"2018-06-28T10:48:09",-0.24,-0.2919230769230769]
[6,28,2018,10,48,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:48:19",-0.25,-0.29076923076923078]
[6,28,2018,10,48,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:48:29",-0.26,-0.29076923076923078]
[6,28,2018,10,48,39,-0.39,-0.39,"2018-06-28T10:48:39",-0.28499999999999998,-0.29538461538461541]
[6,28,2018,10,48,49,-0.39,-0.39,"2018-06-28T10:48:49",-0.31000000000000005,-0.29999999999999993]
[6,28,2018,10,48,59,-0.39,-0.39,"2018-06-28T10:48:59",-0.33500000000000002,-0.30230769230769228]
[6,28,2018,10,49,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T10:49:09",-0.36999999999999994,-0.30692307692307685]
[6,28,2018,10,49,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T10:49:19",-0.39500000000000002,-0.3092307692307692]
[6,28,2018,10,49,29,-0.48,-0.48,"2018-06-28T10:49:29",-0.42499999999999999,-0.315]
[6,28,2018,10,49,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:49:39",-0.41,-0.31269230769230771]
[6,28,2018,10,49,49,-0.24,-0.24,"2018-06-28T10:49:49",-0.38500000000000006,-0.30807692307692308]
[6,28,2018,10,49,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T10:49:59",-0.34499999999999997,-0.3]
[6,28,2018,10,50,9,-0.33,-0.33,"2018-06-28T10:50:09",-0.32500000000000001,-0.29884615384615387]
[6,28,2018,10,50,19,-0.27,-0.27,"2018-06-28T10:50:19",-0.29499999999999998,-0.29538461538461547]
[6,28,2018,10,50,29,-0.24,-0.24,"2018-06-28T10:50:29",-0.255,-0.29192307692307701]
[6,28,2018,10,50,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:50:39",-0.24,-0.28961538461538472]
[6,28,2018,10,50,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:50:49",-0.25,-0.29192307692307701]
[6,28,2018,10,50,59,-0.27,-0.27,"2018-06-28T10:50:59",-0.27,-0.29423076923076924]
[6,28,2018,10,51,9,-0.27,-0.27,"2018-06-28T10:51:09",-0.26,-0.29653846153846158]
[6,28,2018,10,51,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:51:19",-0.26500000000000001,-0.29769230769230764]
[6,28,2018,10,51,29,-0.33,-0.33,"2018-06-28T10:51:29",-0.28000000000000003,-0.3]
[6,28,2018,10,51,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:51:39",-0.29500000000000004,-0.30230769230769228]
[6,28,2018,10,51,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T10:51:49",-0.27,-0.29884615384615387]
[6,28,2018,10,51,59,-0.12,-0.12,"2018-06-28T10:51:59",-0.24500000000000002,-0.2942307692307693]
[6,28,2018,10,52,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T10:52:09",-0.22500000000000001,-0.29076923076923084]
[6,28,2018,10,52,19,-0.24,-0.24,"2018-06-28T10:52:19",-0.21500000000000005,-0.29076923076923084]
[6,28,2018,10,52,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:52:29",-0.19500000000000003,-0.28961538461538461]
[6,28,2018,10,52,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:52:39",-0.18000000000000002,-0.28615384615384615]
[6,28,2018,10,52,49,-0.33,-0.33,"2018-06-28T10:52:49",-0.21,-0.28730769230769232]
[6,28,2018,10,52,59,-0.27,-0.27,"2018-06-28T10:52:59",-0.23500000000000001,-0.28269230769230774]
[6,28,2018,10,53,9,-0.27,-0.27,"2018-06-28T10:53:09",-0.255,-0.27807692307692311]
[6,28,2018,10,53,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:53:19",-0.25,-0.27115384615384613]
[6,28,2018,10,53,29,-0.24,-0.24,"2018-06-28T10:53:29",-0.255,-0.2630769230769231]
[6,28,2018,10,53,39,-0.27,-0.27,{"$f":"DATE(C889,A889,B889)+TIME(D889,E889,F889)","v":"2018-06-28T10:53:39"},-0.26500000000000001,-0.25615384615384618]
[6,28,2018,10,53,49,-0.18,-0.18,"2018-06-28T10:53:49",-0.24,-0.2446153846153846]
[6,28,2018,10,53,59,-0.27,-0.27,"2018-06-28T10:53:59",-0.24,-0.24346153846153845]
[6,28,2018,10,54,9,-0.24,-0.24,"2018-06-28T10:54:09",-0.23499999999999999,-0.24346153846153845]
[6,28,2018,10,54,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T10:54:19",{"$f":"AVERAGE(G888:G893)","v":-0.22500000000000001},-0.24346153846153845]
[6,28,2018,10,54,29,-0.03,-0.03,"2018-06-28T10:54:29",-0.18999999999999997,-0.23192307692307693]
[6,28,2018,10,54,39,-0.06,-0.06,"2018-06-28T10:54:39",-0.155,-0.22384615384615386]
[6,28,2018,10,54,49,-0.06,-0.06,"2018-06-28T10:54:49",-0.13500000000000001,-0.21692307692307691]
[6,28,2018,10,54,59,-0.18,-0.18,"2018-06-28T10:54:59",-0.12,-0.21576923076923077]
[6,28,2018,10,55,9,-0.18,-0.18,"2018-06-28T10:55:09",-0.11,-0.21115384615384614]
[6,28,2018,10,55,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:55:19",-0.12,-0.20884615384615385]
[6,28,2018,10,55,29,-0.12,-0.12,"2018-06-28T10:55:29",-0.13499999999999998,-0.2030769230769231]
[6,28,2018,10,55,39,-0.06,-0.06,"2018-06-28T10:55:39",-0.13500000000000001,-0.19384615384615381]
[6,28,2018,10,55,49,-0.24,-0.24,"2018-06-28T10:55:49",-0.16500000000000001,-0.19038461538461535]
[6,28,2018,10,55,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:55:59",-0.17,-0.18692307692307694]
[6,28,2018,10,56,9,-0.27,-0.27,"2018-06-28T10:56:09",-0.18500000000000003,-0.19153846153846155]
[6,28,2018,10,56,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T10:56:19",-0.18500000000000003,-0.19499999999999998]
[6,28,2018,10,56,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T10:56:29",-0.19000000000000003,-0.19500000000000003]
[6,28,2018,10,56,39,-0.12,-0.12,"2018-06-28T10:56:39",-0.20000000000000004,-0.19038461538461543]
[6,28,2018,10,56,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T10:56:49",-0.18500000000000003,-0.18807692307692309]
[6,28,2018,10,56,59,-0.06,-0.06,"2018-06-28T10:56:59",-0.16000000000000003,-0.18230769230769234]
[6,28,2018,10,57,9,-0.06,-0.06,"2018-06-28T10:57:09",-0.12500000000000003,-0.1719230769230769]
[6,28,2018,10,57,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T10:57:19",-0.115,-0.16730769230769232]
[6,28,2018,10,57,29,-0.09,-0.09,"2018-06-28T10:57:29",-0.105,-0.16038461538461538]
[6,28,2018,10,57,39,-0.09,-0.09,"2018-06-28T10:57:39",-9.9999999999999992E-2,{"$f":"AVERAGE(G888:G913)","v":-0.15576923076923077}]
[6,28,2018,10,57,49,0,0,"2018-06-28T10:57:49",-7.4999999999999997E-2,-0.14653846153846153]
[6,28,2018,10,57,59,0,0,"2018-06-28T10:57:59",-6.5000000000000002E-2,-0.13615384615384613]
[6,28,2018,10,58,9,-0.03,-0.03,"2018-06-28T10:58:09",-0.06,-0.13038461538461538]
[6,28,2018,10,58,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T10:58:19",-0.06,-0.12576923076923074]
[6,28,2018,10,58,29,-0.27,-0.27,"2018-06-28T10:58:29",-9.0000000000000011E-2,-0.12692307692307689]
[6,28,2018,10,58,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:58:39",-0.12500000000000003,-0.13269230769230766]
[6,28,2018,10,58,49,-0.18,-0.18,"2018-06-28T10:58:49",-0.15500000000000003,-0.13846153846153844]
[6,28,2018,10,58,59,-0.18,-0.18,"2018-06-28T10:58:59",-0.18500000000000003,-0.14307692307692307]
[6,28,2018,10,59,9,-0.18,-0.18,"2018-06-28T10:59:09",-0.21,-0.14769230769230771]
[6,28,2018,10,59,19,-0.09,-0.09,"2018-06-28T10:59:19",-0.19999999999999998,-0.14423076923076922]
[6,28,2018,10,59,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T10:59:29",-0.20499999999999999,-0.14884615384615385]
[6,28,2018,10,59,39,-0.39,-0.39,"2018-06-28T10:59:39",-0.22,-0.1557692307692308]
[6,28,2018,10,59,49,-0.18,-0.18,"2018-06-28T10:59:49",-0.22,-0.15807692307692311]
[6,28,2018,10,59,59,-0.06,-0.06,"2018-06-28T10:59:59",-0.20000000000000004,-0.15807692307692311]
[6,28,2018,11,0,9,-0.06,-0.06,"2018-06-28T11:00:09",-0.18000000000000002,-0.15115384615384622]
[6,28,2018,11,0,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:00:19",-0.19000000000000003,-0.14884615384615391]
[6,28,2018,11,0,29,-0.18,-0.18,"2018-06-28T11:00:29",-0.17000000000000004,-0.14538461538461542]
[6,28,2018,11,0,39,-0.06,-0.06,"2018-06-28T11:00:39",-0.11499999999999999,-0.13961538461538464]
[6,28,2018,11,0,49,-0.09,-0.09,"2018-06-28T11:00:49",-9.9999999999999992E-2,-0.1373076923076923]
[6,28,2018,11,0,59,-0.12,-0.12,"2018-06-28T11:00:59",-0.11,-0.13730769230769233]
[6,28,2018,11,1,9,-0.18,-0.18,"2018-06-28T11:01:09",-0.13,-0.13846153846153847]
[6,28,2018,11,1,19,-0.27,-0.27,"2018-06-28T11:01:19",-0.15,-0.14653846153846156]
[6,28,2018,11,1,29,-0.39,-0.39,"2018-06-28T11:01:29",-0.18499999999999997,-0.15923076923076926]
[6,28,2018,11,1,39,-0.33,-0.33,"2018-06-28T11:01:39",-0.23,-0.16615384615384615]
[6,28,2018,11,1,49,-0.39,-0.39,"2018-06-28T11:01:49",-0.28000000000000003,-0.1776923076923077]
[6,28,2018,11,1,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:01:59",-0.31,-0.18576923076923077]
[6,28,2018,11,2,9,-0.33,-0.33,"2018-06-28T11:02:09",-0.33499999999999996,-0.19846153846153847]
[6,28,2018,11,2,19,-0.39,-0.39,"2018-06-28T11:02:19",-0.35499999999999998,-0.21346153846153845]
[6,28,2018,11,2,29,-0.36,-0.36,"2018-06-28T11:02:29",-0.35000000000000003,-0.22615384615384615]
[6,28,2018,11,2,39,-0.24,-0.24,"2018-06-28T11:02:39",-0.33499999999999996,-0.22961538461538464]
[6,28,2018,11,2,49,-0.09,-0.09,"2018-06-28T11:02:49",-0.28499999999999998,-0.22269230769230772]
[6,28,2018,11,2,59,-0.06,-0.06,"2018-06-28T11:02:59",-0.24500000000000002,-0.21346153846153845]
[6,28,2018,11,3,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:03:09",-0.215,-0.21230769230769236]
[6,28,2018,11,3,19,-0.27,-0.27,"2018-06-28T11:03:19",-0.19499999999999998,-0.21576923076923082]
[6,28,2018,11,3,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:03:29",-0.18500000000000003,-0.22038461538461537]
[6,28,2018,11,3,39,-0.27,-0.27,"2018-06-28T11:03:39",-0.19000000000000003,-0.22730769230769232]
[6,28,2018,11,3,49,-0.27,-0.27,"2018-06-28T11:03:49",-0.22,-0.22615384615384618]
[6,28,2018,11,3,59,-0.24,-0.24,"2018-06-28T11:03:59",-0.25000000000000006,-0.2203846153846154]
[6,28,2018,11,4,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:04:09",-0.26,-0.22153846153846157]
[6,28,2018,11,4,19,-0.09,-0.09,{"$f":"DATE(C953,A953,B953)+TIME(D953,E953,F953)","v":"2018-06-28T11:04:19"},-0.23,-0.22269230769230769]
[6,28,2018,11,4,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:04:29",-0.215,-0.22846153846153844]
[6,28,2018,11,4,39,-0.18,-0.18,"2018-06-28T11:04:39",-0.19999999999999998,-0.22961538461538464]
[6,28,2018,11,4,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:04:49",-0.18999999999999997,-0.23076923076923073]
[6,28,2018,11,4,59,-0.12,-0.12,"2018-06-28T11:04:59",{"$f":"AVERAGE(G952:G957)","v":-0.17},-0.2330769230769231]
[6,28,2018,11,5,9,-0.12,-0.12,"2018-06-28T11:05:09",-0.155,-0.23423076923076919]
[6,28,2018,11,5,19,-0.12,-0.12,"2018-06-28T11:05:19",-0.16,-0.23423076923076921]
[6,28,2018,11,5,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:05:29",-0.15,-0.2330769230769231]
[6,28,2018,11,5,39,-0.24,-0.24,"2018-06-28T11:05:39",-0.16,-0.23192307692307693]
[6,28,2018,11,5,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:05:49",-0.16,-0.22500000000000003]
[6,28,2018,11,5,59,-0.27,-0.27,"2018-06-28T11:05:59",-0.18500000000000003,-0.22269230769230772]
[6,28,2018,11,6,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:06:09",-0.215,-0.21923076923076931]
[6,28,2018,11,6,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:06:19",-0.23,-0.21576923076923082]
[6,28,2018,11,6,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:06:29",-0.24,-0.21115384615384614]
[6,28,2018,11,6,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:06:39",-0.25,-0.2076923076923077]
[6,28,2018,11,6,49,-0.33,-0.33,"2018-06-28T11:06:49",-0.27,-0.2065384615384615]
[6,28,2018,11,6,59,-0.27,-0.27,"2018-06-28T11:06:59",-0.27,-0.2076923076923077]
[6,28,2018,11,7,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:07:09",-0.27,-0.21576923076923077]
[6,28,2018,11,7,19,-0.39,-0.39,"2018-06-28T11:07:19",-0.30000000000000004,-0.22846153846153844]
[6,28,2018,11,7,29,-0.33,-0.33,"2018-06-28T11:07:29",-0.32000000000000006,-0.23538461538461536]
[6,28,2018,11,7,39,-0.33,-0.33,"2018-06-28T11:07:39",-0.32500000000000001,-0.23769230769230767]
[6,28,2018,11,7,49,-0.39,-0.39,"2018-06-28T11:07:49",-0.33500000000000002,-0.24115384615384611]
[6,28,2018,11,7,59,-0.39,-0.39,"2018-06-28T11:07:59",-0.35500000000000004,-0.24576923076923071]
[6,28,2018,11,8,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T11:08:09",-0.375,-0.25153846153846149]
[6,28,2018,11,8,19,-0.54,-0.54,"2018-06-28T11:08:19",-0.39999999999999997,{"$f":"AVERAGE(G952:G977)","v":-0.26307692307692304}]
[6,28,2018,11,8,29,-0.48,-0.48,"2018-06-28T11:08:29",-0.42499999999999999,-0.27346153846153842]
[6,28,2018,11,8,39,-0.44999999999999996,-0.44999999999999996,"2018-06-28T11:08:39",-0.44500000000000001,-0.28730769230769232]
[6,28,2018,11,8,49,-0.48,-0.48,"2018-06-28T11:08:49",-0.46,-0.2976923076923077]
[6,28,2018,11,8,59,-0.39,-0.39,"2018-06-28T11:08:59",-0.46,-0.30576923076923068]
[6,28,2018,11,9,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T11:09:09",-0.45999999999999996,-0.31384615384615383]
[6,28,2018,11,9,19,-0.48,-0.48,"2018-06-28T11:09:19",-0.44999999999999996,-0.32769230769230767]
[6,28,2018,11,9,29,-0.39,-0.39,"2018-06-28T11:09:29",-0.435,-0.33807692307692305]
[6,28,2018,11,9,39,-0.39,-0.39,"2018-06-28T11:09:39",-0.42500000000000004,-0.34846153846153849]
[6,28,2018,11,9,49,-0.36,-0.36,"2018-06-28T11:09:49",-0.40500000000000003,-0.35653846153846153]
[6,28,2018,11,9,59,-0.44999999999999996,-0.44999999999999996,"2018-06-28T11:09:59",-0.41500000000000004,-0.36461538461538456]
[6,28,2018,11,10,9,-0.39,-0.39,"2018-06-28T11:10:09",-0.41000000000000009,-0.37153846153846154]
[6,28,2018,11,10,19,-0.48,-0.48,"2018-06-28T11:10:19",-0.41,-0.37961538461538458]
[6,28,2018,11,10,29,-0.48,-0.48,"2018-06-28T11:10:29",-0.42499999999999999,-0.3865384615384615]
[6,28,2018,11,10,39,-0.54,-0.54,"2018-06-28T11:10:39",-0.45,-0.39923076923076917]
[6,28,2018,11,10,49,-0.48,-0.48,"2018-06-28T11:10:49",-0.47,-0.40961538461538471]
[6,28,2018,11,10,59,-0.36,-0.36,"2018-06-28T11:10:59",-0.45500000000000002,-0.41192307692307695]
[6,28,2018,11,11,9,-0.24,-0.24,"2018-06-28T11:11:09",-0.43,-0.40846153846153843]
[6,28,2018,11,11,19,-0.09,-0.09,"2018-06-28T11:11:19",-0.36499999999999994,-0.40153846153846151]
[6,28,2018,11,11,29,-0.09,-0.09,"2018-06-28T11:11:29",-0.3,-0.39346153846153842]
[6,28,2018,11,11,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:11:39",-0.24500000000000002,-0.3865384615384615]
[6,28,2018,11,11,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:11:49",-0.19999999999999998,-0.38192307692307698]
[6,28,2018,11,11,59,-0.24,-0.24,"2018-06-28T11:11:59",-0.17999999999999997,-0.37846153846153846]
[6,28,2018,11,12,9,-0.24,-0.24,"2018-06-28T11:12:09",-0.18000000000000002,-0.37269230769230777]
[6,28,2018,11,12,19,-0.18,-0.18,"2018-06-28T11:12:19",-0.19499999999999998,-0.36461538461538462]
[6,28,2018,11,12,29,-0.33,-0.33,"2018-06-28T11:12:29",-0.23500000000000001,-0.36115384615384616]
[6,28,2018,11,12,39,-0.27,-0.27,"2018-06-28T11:12:39",-0.245,-0.35076923076923072]
[6,28,2018,11,12,49,-0.27,-0.27,"2018-06-28T11:12:49",-0.255,-0.34269230769230768]
[6,28,2018,11,12,59,-0.24,-0.24,"2018-06-28T11:12:59",-0.255,-0.33461538461538465]
[6,28,2018,11,13,9,-0.27,-0.27,"2018-06-28T11:13:09",-0.26,-0.32653846153846156]
[6,28,2018,11,13,19,-0.27,-0.27,"2018-06-28T11:13:19",-0.27500000000000002,-0.32192307692307698]
[6,28,2018,11,13,29,-0.27,-0.27,"2018-06-28T11:13:29",-0.26500000000000001,-0.31615384615384612]
[6,28,2018,11,13,39,-0.24,-0.24,"2018-06-28T11:13:39",-0.26,-0.30692307692307685]
[6,28,2018,11,13,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:13:49",-0.25,-0.29999999999999993]
[6,28,2018,11,13,59,-0.18,-0.18,"2018-06-28T11:13:59",-0.24,-0.2919230769230769]
[6,28,2018,11,14,9,-0.18,-0.18,"2018-06-28T11:14:09",-0.22499999999999998,-0.28499999999999992]
[6,28,2018,11,14,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:14:19",-0.20499999999999999,-0.27346153846153842]
[6,28,2018,11,14,29,-0.09,-0.09,"2018-06-28T11:14:29",-0.17500000000000002,-0.26192307692307681]
[6,28,2018,11,14,39,-0.03,-0.03,"2018-06-28T11:14:39",-0.14000000000000001,-0.2446153846153846]
[6,28,2018,11,14,49,0,0,"2018-06-28T11:14:49",-0.105,-0.22615384615384612]
[6,28,2018,11,14,59,-0.12,-0.12,{"$f":"DATE(C1017,A1017,B1017)+TIME(D1017,E1017,F1017)","v":"2018-06-28T11:14:59"},-9.5000000000000015E-2,-0.21]
[6,28,2018,11,15,9,-0.06,-0.06,"2018-06-28T11:15:09",-7.4999999999999997E-2,-0.19384615384615381]
[6,28,2018,11,15,19,-0.12,-0.12,"2018-06-28T11:15:19",-6.9999999999999993E-2,-0.18461538461538457]
[6,28,2018,11,15,29,-0.09,-0.09,"2018-06-28T11:15:29",-6.9999999999999993E-2,-0.17884615384615385]
[6,28,2018,11,15,39,-0.09,-0.09,"2018-06-28T11:15:39",{"$f":"AVERAGE(G1016:G1021)","v":-0.08},-0.17884615384615385]
[6,28,2018,11,15,49,-0.12,-0.12,"2018-06-28T11:15:49",-9.9999999999999992E-2,-0.18000000000000002]
[6,28,2018,11,15,59,-0.06,-0.06,"2018-06-28T11:15:59",-9.0000000000000011E-2,-0.17423076923076922]
[6,28,2018,11,16,9,-0.09,-0.09,"2018-06-28T11:16:09",-9.4999999999999987E-2,-0.16961538461538461]
[6,28,2018,11,16,19,-0.12,-0.12,"2018-06-28T11:16:19",-9.4999999999999987E-2,-0.16499999999999998]
[6,28,2018,11,16,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:16:29",-0.11499999999999999,-0.16384615384615384]
[6,28,2018,11,16,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:16:39",-0.12500000000000003,-0.16269230769230772]
[6,28,2018,11,16,49,-0.09,-0.09,"2018-06-28T11:16:49",-0.12000000000000001,-0.15346153846153845]
[6,28,2018,11,16,59,-0.06,-0.06,"2018-06-28T11:16:59",-0.12,-0.14538461538461536]
[6,28,2018,11,17,9,-0.03,-0.03,"2018-06-28T11:17:09",-0.11000000000000003,-0.13615384615384613]
[6,28,2018,11,17,19,0.06,0.06,"2018-06-28T11:17:19",-0.08,-0.1246153846153846]
[6,28,2018,11,17,29,0.03,0.03,"2018-06-28T11:17:29",-4.0000000000000015E-2,-0.11307692307692307]
[6,28,2018,11,17,39,-0.18,-0.18,"2018-06-28T11:17:39",-4.5000000000000005E-2,-0.10961538461538464]
[6,28,2018,11,17,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:17:49",-0.08,-0.1107692307692308]
[6,28,2018,11,17,59,-0.24,-0.24,"2018-06-28T11:17:59",-0.11,-0.1107692307692308]
[6,28,2018,11,18,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:18:09",-0.155,-0.11423076923076922]
[6,28,2018,11,18,19,-0.27,-0.27,"2018-06-28T11:18:19",-0.21000000000000005,-0.11769230769230769]
[6,28,2018,11,18,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:18:29",-0.26500000000000001,-0.12230769230769233]
[6,28,2018,11,18,39,-0.33,-0.33,"2018-06-28T11:18:39",-0.29000000000000004,-0.12923076923076923]
[6,28,2018,11,18,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:18:49",-0.29000000000000004,-0.13730769230769233]
[6,28,2018,11,18,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:18:59",-0.27500000000000008,{"$f":"AVERAGE(G1016:G1041)","v":-0.14192307692307693}]
[6,28,2018,11,19,9,-0.03,-0.03,"2018-06-28T11:19:09",-0.23,-0.14307692307692307]
[6,28,2018,11,19,19,-0.06,-0.06,"2018-06-28T11:19:19",-0.19500000000000003,-0.14076923076923076]
[6,28,2018,11,19,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:19:29",-0.17,-0.14423076923076922]
[6,28,2018,11,19,39,-0.12,-0.12,"2018-06-28T11:19:39",-0.13500000000000001,-0.14423076923076922]
[6,28,2018,11,19,49,-0.03,-0.03,"2018-06-28T11:19:49",-9.0000000000000011E-2,-0.14192307692307687]
[6,28,2018,11,19,59,-0.03,-0.03,"2018-06-28T11:19:59",-7.0000000000000007E-2,-0.13961538461538459]
[6,28,2018,11,20,9,-0.03,-0.03,"2018-06-28T11:20:09",-7.0000000000000007E-2,-0.1361538461538461]
[6,28,2018,11,20,19,-0.06,-0.06,"2018-06-28T11:20:19",-7.0000000000000021E-2,-0.13615384615384613]
[6,28,2018,11,20,29,-0.03,-0.03,"2018-06-28T11:20:29",-5.000000000000001E-2,-0.13384615384615381]
[6,28,2018,11,20,39,0.03,0.03,"2018-06-28T11:20:39",-2.4999999999999998E-2,-0.12807692307692303]
[6,28,2018,11,20,49,0.03,0.03,"2018-06-28T11:20:49",-1.4999999999999999E-2,-0.11884615384615382]
[6,28,2018,11,20,59,0,0,"2018-06-28T11:20:59",-0.01,-0.11307692307692307]
[6,28,2018,11,21,9,-0.03,-0.03,"2018-06-28T11:21:09",-0.01,-0.11076923076923074]
[6,28,2018,11,21,19,0.03,0.03,"2018-06-28T11:21:19",5.0000000000000001E-3,-0.1073076923076923]
[6,28,2018,11,21,29,0.03,0.03,"2018-06-28T11:21:29",1.4999999999999999E-2,-0.105]
[6,28,2018,11,21,39,0,0,"2018-06-28T11:21:39",0.01,-0.10730769230769231]
[6,28,2018,11,21,49,-0.06,-0.06,"2018-06-28T11:21:49",-5.0000000000000001E-3,-0.11076923076923076]
[6,28,2018,11,21,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:21:59",-3.0000000000000002E-2,-0.1096153846153846]
[6,28,2018,11,22,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:22:09",-5.000000000000001E-2,-0.10384615384615385]
[6,28,2018,11,22,19,-0.09,-0.09,"2018-06-28T11:22:19",-7.0000000000000007E-2,-9.8076923076923089E-2]
[6,28,2018,11,22,29,0,0,"2018-06-28T11:22:29",-7.5000000000000011E-2,-8.653846153846155E-2]
[6,28,2018,11,22,39,-0.06,-0.06,"2018-06-28T11:22:39",-8.5000000000000006E-2,-7.8461538461538485E-2]
[6,28,2018,11,22,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:22:49",-0.10000000000000002,-7.2692307692307709E-2]
[6,28,2018,11,22,59,-0.09,-0.09,"2018-06-28T11:22:59",-9.0000000000000011E-2,-6.3461538461538486E-2]
[6,28,2018,11,23,9,-0.03,-0.03,"2018-06-28T11:23:09",-7.0000000000000007E-2,-5.3076923076923091E-2]
[6,28,2018,11,23,19,-0.12,-0.12,"2018-06-28T11:23:19",-7.5000000000000011E-2,-5.1923076923076926E-2]
[6,28,2018,11,23,29,-0.12,-0.12,"2018-06-28T11:23:29",-9.5000000000000015E-2,-5.53846153846154E-2]
[6,28,2018,11,23,39,-0.18,-0.18,"2018-06-28T11:23:39",-0.11499999999999999,-6.0000000000000012E-2]
[6,28,2018,11,23,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:23:49",-0.125,-6.23076923076923E-2]
[6,28,2018,11,23,59,-0.33,-0.33,"2018-06-28T11:23:59",-0.16500000000000001,-7.0384615384615393E-2]
[6,28,2018,11,24,9,-0.33,-0.33,"2018-06-28T11:24:09",-0.215,-8.1923076923076918E-2]
[6,28,2018,11,24,19,-0.39,-0.39,"2018-06-28T11:24:19",-0.26,-9.5769230769230773E-2]
[6,28,2018,11,24,29,-0.27,-0.27,"2018-06-28T11:24:29",-0.28499999999999998,-0.105]
[6,28,2018,11,24,39,-0.27,-0.27,"2018-06-28T11:24:39",-0.30000000000000004,-0.11307692307692309]
[6,28,2018,11,24,49,-0.06,-0.06,"2018-06-28T11:24:49",-0.27500000000000002,-0.11423076923076923]
[6,28,2018,11,24,59,-0.09,-0.09,"2018-06-28T11:24:59",-0.23500000000000001,-0.11884615384615385]
[6,28,2018,11,25,9,-0.09,-0.09,"2018-06-28T11:25:09",-0.19500000000000003,-0.12346153846153846]
[6,28,2018,11,25,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:25:19",-0.155,-0.12923076923076923]
[6,28,2018,11,25,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:25:29",-0.14500000000000002,-0.13615384615384615]
[6,28,2018,11,25,39,-0.21000000000000002,-0.21000000000000002,{"$f":"DATE(C1081,A1081,B1081)+TIME(D1081,E1081,F1081)","v":"2018-06-28T11:25:39"},-0.13500000000000001,-0.14538461538461539]
[6,28,2018,11,25,49,-0.42000000000000004,-0.42000000000000004,"2018-06-28T11:25:49",-0.19499999999999998,-0.16269230769230766]
[6,28,2018,11,25,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T11:25:59",-0.25,-0.17884615384615382]
[6,28,2018,11,26,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T11:26:09",-0.30499999999999999,-0.19269230769230769]
[6,28,2018,11,26,19,-0.36,-0.36,"2018-06-28T11:26:19",{"$f":"AVERAGE(G1080:G1085)","v":-0.34},-0.20076923076923076]
[6,28,2018,11,26,29,-0.33,-0.33,"2018-06-28T11:26:29",-0.36000000000000004,-0.2076923076923077]
[6,28,2018,11,26,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T11:26:39",-0.39500000000000002,-0.2203846153846154]
[6,28,2018,11,26,49,-0.39,-0.39,"2018-06-28T11:26:49",-0.39000000000000007,-0.23538461538461539]
[6,28,2018,11,26,59,-0.24,-0.24,"2018-06-28T11:26:59",-0.36000000000000004,-0.24230769230769231]
[6,28,2018,11,27,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:27:09",-0.315,-0.24230769230769234]
[6,28,2018,11,27,19,-0.12,-0.12,"2018-06-28T11:27:19",-0.27500000000000008,-0.24346153846153845]
[6,28,2018,11,27,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:27:29",-0.25500000000000006,-0.25038461538461543]
[6,28,2018,11,27,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T11:27:39",-0.25500000000000006,-0.26192307692307693]
[6,28,2018,11,27,49,-0.54,-0.54,"2018-06-28T11:27:49",-0.28000000000000003,-0.27807692307692311]
[6,28,2018,11,27,59,-0.48,-0.48,"2018-06-28T11:27:59",-0.32,-0.28961538461538466]
[6,28,2018,11,28,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T11:28:09",-0.36999999999999994,-0.29884615384615387]
[6,28,2018,11,28,19,-0.27,-0.27,"2018-06-28T11:28:19",-0.39500000000000002,-0.29653846153846158]
[6,28,2018,11,28,29,-0.27,-0.27,"2018-06-28T11:28:29",-0.40500000000000003,-0.29423076923076924]
[6,28,2018,11,28,39,-0.27,-0.27,"2018-06-28T11:28:39",-0.37999999999999995,-0.28961538461538461]
[6,28,2018,11,28,49,-0.39,-0.39,"2018-06-28T11:28:49",-0.35499999999999998,-0.29423076923076918]
[6,28,2018,11,28,59,-0.39,-0.39,"2018-06-28T11:28:59",-0.34,-0.29884615384615376]
[6,28,2018,11,29,9,-0.54,-0.54,"2018-06-28T11:29:09",-0.35500000000000004,-0.31730769230769229]
[6,28,2018,11,29,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T11:29:19",-0.38500000000000001,-0.33115384615384613]
[6,28,2018,11,29,29,-0.51,-0.51,"2018-06-28T11:29:29",-0.42499999999999999,-0.34730769230769226]
[6,28,2018,11,29,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T11:29:39",-0.45,{"$f":"AVERAGE(G1080:G1105)","v":-0.35769230769230764}]
[6,28,2018,11,29,49,-0.27,-0.27,"2018-06-28T11:29:49",-0.43,-0.36]
[6,28,2018,11,29,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:29:59",-0.38999999999999996,-0.35769230769230764]
[6,28,2018,11,30,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:30:09",-0.33499999999999996,-0.34961538461538461]
[6,28,2018,11,30,19,-0.12,-0.12,"2018-06-28T11:30:19",-0.28000000000000003,-0.33807692307692305]
[6,28,2018,11,30,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:30:29",-0.21999999999999997,-0.32769230769230767]
[6,28,2018,11,30,39,-0.06,-0.06,"2018-06-28T11:30:39",-0.16000000000000003,-0.31615384615384612]
[6,28,2018,11,30,49,0,0,"2018-06-28T11:30:49",-0.11500000000000003,-0.30346153846153845]
[6,28,2018,11,30,59,-0.09,-0.09,"2018-06-28T11:30:59",-0.105,-0.29076923076923078]
[6,28,2018,11,31,9,-0.12,-0.12,"2018-06-28T11:31:09",-9.0000000000000011E-2,-0.2803846153846154]
[6,28,2018,11,31,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:31:19",-9.5000000000000015E-2,-0.27692307692307694]
[6,28,2018,11,31,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:31:29",-9.5000000000000015E-2,-0.27692307692307694]
[6,28,2018,11,31,39,-0.09,-0.09,"2018-06-28T11:31:39",-9.9999999999999992E-2,-0.27576923076923082]
[6,28,2018,11,31,49,-0.12,-0.12,"2018-06-28T11:31:49",-0.12,-0.27230769230769236]
[6,28,2018,11,31,59,-0.24,-0.24,"2018-06-28T11:31:59",-0.14499999999999999,-0.26538461538461544]
[6,28,2018,11,32,9,-0.27,-0.27,"2018-06-28T11:32:09",-0.17,-0.255]
[6,28,2018,11,32,19,-0.24,-0.24,"2018-06-28T11:32:19",-0.18499999999999997,-0.24576923076923085]
[6,28,2018,11,32,29,-0.18,-0.18,"2018-06-28T11:32:29",-0.18999999999999997,-0.23538461538461541]
[6,28,2018,11,32,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:32:39",-0.20000000000000004,-0.23076923076923084]
[6,28,2018,11,32,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:32:49",-0.215,-0.22846153846153847]
[6,28,2018,11,32,59,-0.12,-0.12,"2018-06-28T11:32:59",-0.19499999999999998,-0.22269230769230772]
[6,28,2018,11,33,9,-0.12,-0.12,"2018-06-28T11:33:09",-0.17,-0.21230769230769234]
[6,28,2018,11,33,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:33:19",-0.16500000000000001,-0.20538461538461539]
[6,28,2018,11,33,29,-0.33,-0.33,"2018-06-28T11:33:29",-0.19000000000000003,-0.1973076923076923]
[6,28,2018,11,33,39,-0.33,-0.33,"2018-06-28T11:33:39",-0.22,-0.19269230769230769]
[6,28,2018,11,33,49,-0.36,-0.36,"2018-06-28T11:33:49",-0.24500000000000002,-0.18692307692307694]
[6,28,2018,11,33,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:33:59",-0.26,-0.1788461538461539]
[6,28,2018,11,34,9,-0.18,-0.18,"2018-06-28T11:34:09",-0.26999999999999996,-0.17538461538461542]
[6,28,2018,11,34,19,-0.06,-0.06,"2018-06-28T11:34:19",-0.245,-0.1719230769230769]
[6,28,2018,11,34,29,-0.12,-0.12,"2018-06-28T11:34:29",-0.20999999999999996,-0.16846153846153847]
[6,28,2018,11,34,39,-0.24,-0.24,"2018-06-28T11:34:39",-0.19499999999999998,-0.17307692307692307]
[6,28,2018,11,34,49,-0.18,-0.18,"2018-06-28T11:34:49",-0.16500000000000001,-0.17423076923076924]
[6,28,2018,11,34,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:34:59",-0.16500000000000001,-0.18]
[6,28,2018,11,35,9,-0.33,-0.33,"2018-06-28T11:35:09",-0.19000000000000003,-0.19269230769230769]
[6,28,2018,11,35,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:35:19",-0.20499999999999999,-0.19500000000000001]
[6,28,2018,11,35,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:35:29",-0.23499999999999999,-0.20192307692307693]
[6,28,2018,11,35,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:35:39",-0.245,-0.2076923076923077]
[6,28,2018,11,35,49,-0.27,-0.27,"2018-06-28T11:35:49",-0.26,-0.21230769230769236]
[6,28,2018,11,35,59,-0.27,-0.27,"2018-06-28T11:35:59",-0.27,-0.21923076923076928]
[6,28,2018,11,36,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:36:09",-0.24,-0.2203846153846154]
[6,28,2018,11,36,19,-0.12,-0.12,{"$f":"DATE(C1145,A1145,B1145)+TIME(D1145,E1145,F1145)","v":"2018-06-28T11:36:19"},-0.23500000000000001,-0.21576923076923077]
[6,28,2018,11,36,29,-0.06,-0.06,"2018-06-28T11:36:29",-0.19500000000000003,-0.2076923076923077]
[6,28,2018,11,36,39,-0.09,-0.09,"2018-06-28T11:36:39",-0.16,-0.20192307692307693]
[6,28,2018,11,36,49,0,0,"2018-06-28T11:36:49",-0.115,-0.19500000000000001]
[6,28,2018,11,36,59,-0.03,-0.03,"2018-06-28T11:36:59",{"$f":"AVERAGE(G1144:G1149)","v":-7.5000000000000011E-2},-0.1903846153846154]
[6,28,2018,11,37,9,-0.09,-0.09,"2018-06-28T11:37:09",-6.5000000000000002E-2,-0.18576923076923074]
[6,28,2018,11,37,19,-0.09,-0.09,"2018-06-28T11:37:19",-0.06,-0.1846153846153846]
[6,28,2018,11,37,29,-0.18,-0.18,"2018-06-28T11:37:29",-0.08,-0.18692307692307691]
[6,28,2018,11,37,39,-0.18,-0.18,"2018-06-28T11:37:39",-9.5000000000000015E-2,-0.18576923076923071]
[6,28,2018,11,37,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:37:49",-0.13,-0.18115384615384611]
[6,28,2018,11,37,59,-0.24,-0.24,"2018-06-28T11:37:59",-0.16500000000000001,-0.17769230769230765]
[6,28,2018,11,38,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:38:09",-0.17500000000000002,-0.16961538461538467]
[6,28,2018,11,38,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:38:19",-0.18500000000000003,-0.16730769230769232]
[6,28,2018,11,38,29,-0.12,-0.12,"2018-06-28T11:38:29",-0.17500000000000002,-0.16500000000000004]
[6,28,2018,11,38,39,-0.06,-0.06,"2018-06-28T11:38:39",-0.15500000000000003,-0.16499999999999998]
[6,28,2018,11,38,49,-0.06,-0.06,"2018-06-28T11:38:49",-0.13,-0.16269230769230764]
[6,28,2018,11,38,59,-0.06,-0.06,"2018-06-28T11:38:59",-0.10000000000000002,-0.15576923076923072]
[6,28,2018,11,39,9,-0.06,-0.06,"2018-06-28T11:39:09",-8.5000000000000006E-2,-0.15115384615384614]
[6,28,2018,11,39,19,-0.06,-0.06,"2018-06-28T11:39:19",-6.9999999999999993E-2,-0.14538461538461539]
[6,28,2018,11,39,29,-0.06,-0.06,"2018-06-28T11:39:29",-0.06,-0.13500000000000004]
[6,28,2018,11,39,39,-0.03,-0.03,"2018-06-28T11:39:39",-5.4999999999999993E-2,-0.13038461538461538]
[6,28,2018,11,39,49,-0.09,-0.09,"2018-06-28T11:39:49",-0.06,-0.12230769230769231]
[6,28,2018,11,39,59,-0.12,-0.12,"2018-06-28T11:39:59",-6.9999999999999993E-2,-0.11538461538461539]
[6,28,2018,11,40,9,-0.18,-0.18,"2018-06-28T11:40:09",-9.0000000000000011E-2,-0.11192307692307693]
[6,28,2018,11,40,19,-0.18,-0.18,"2018-06-28T11:40:19",-0.10999999999999999,{"$f":"AVERAGE(G1144:G1169)","v":-0.10846153846153847}]
[6,28,2018,11,40,29,-0.24,-0.24,"2018-06-28T11:40:29",-0.13999999999999999,-0.11192307692307693]
[6,28,2018,11,40,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:40:39",-0.17,-0.11538461538461542]
[6,28,2018,11,40,49,-0.18,-0.18,"2018-06-28T11:40:49",-0.18499999999999997,-0.12000000000000002]
[6,28,2018,11,40,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:40:59",-0.19000000000000003,-0.12230769230769233]
[6,28,2018,11,41,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:41:09",-0.18500000000000003,-0.12807692307692309]
[6,28,2018,11,41,19,-0.18,-0.18,"2018-06-28T11:41:19",-0.18500000000000003,-0.13384615384615389]
[6,28,2018,11,41,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:41:29",-0.17,-0.13615384615384621]
[6,28,2018,11,41,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:41:39",-0.16,-0.13846153846153847]
[6,28,2018,11,41,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:41:49",-0.15500000000000003,-0.1373076923076923]
[6,28,2018,11,41,59,-0.12,-0.12,"2018-06-28T11:41:59",-0.15000000000000002,-0.13500000000000001]
[6,28,2018,11,42,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:42:09",-0.15000000000000002,-0.13269230769230769]
[6,28,2018,11,42,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:42:19",-0.14500000000000002,-0.12923076923076923]
[6,28,2018,11,42,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:42:29",-0.15500000000000003,-0.13153846153846152]
[6,28,2018,11,42,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:42:39",-0.16500000000000001,-0.13384615384615384]
[6,28,2018,11,42,49,-0.27,-0.27,"2018-06-28T11:42:49",-0.18500000000000003,-0.13961538461538459]
[6,28,2018,11,42,59,-0.33,-0.33,"2018-06-28T11:42:59",-0.22,-0.14999999999999997]
[6,28,2018,11,43,9,-0.33,-0.33,"2018-06-28T11:43:09",-0.25000000000000006,-0.16038461538461535]
[6,28,2018,11,43,19,-0.39,-0.39,"2018-06-28T11:43:19",-0.29000000000000004,-0.17307692307692304]
[6,28,2018,11,43,29,-0.42000000000000004,-0.42000000000000004,"2018-06-28T11:43:29",-0.32500000000000001,-0.18692307692307691]
[6,28,2018,11,43,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T11:43:39",-0.36000000000000004,-0.20076923076923076]
[6,28,2018,11,43,49,-0.63,-0.63,"2018-06-28T11:43:49",-0.42,-0.22269230769230766]
[6,28,2018,11,43,59,-0.60000000000000009,-0.60000000000000009,"2018-06-28T11:43:59",-0.46500000000000002,-0.2446153846153846]
[6,28,2018,11,44,9,-0.57000000000000006,-0.57000000000000006,"2018-06-28T11:44:09",-0.505,-0.2630769230769231]
[6,28,2018,11,44,19,-0.48,-0.48,"2018-06-28T11:44:19",-0.52000000000000013,-0.27692307692307694]
[6,28,2018,11,44,29,-0.36,-0.36,"2018-06-28T11:44:29",-0.51,-0.28384615384615391]
[6,28,2018,11,44,39,-0.39,-0.39,"2018-06-28T11:44:39",-0.505,-0.29192307692307701]
[6,28,2018,11,44,49,-0.57000000000000006,-0.57000000000000006,"2018-06-28T11:44:49",-0.49500000000000011,-0.30461538461538468]
[6,28,2018,11,44,59,-0.57000000000000006,-0.57000000000000006,"2018-06-28T11:44:59",-0.49000000000000005,-0.31846153846153852]
[6,28,2018,11,45,9,-0.60000000000000009,-0.60000000000000009,"2018-06-28T11:45:09",-0.49500000000000005,-0.33461538461538465]
[6,28,2018,11,45,19,-0.57000000000000006,-0.57000000000000006,"2018-06-28T11:45:19",-0.51000000000000012,-0.35076923076923083]
[6,28,2018,11,45,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T11:45:29",-0.52500000000000002,-0.36230769230769239]
[6,28,2018,11,45,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T11:45:39",-0.53000000000000014,-0.37153846153846154]
[6,28,2018,11,45,49,-0.33,-0.33,"2018-06-28T11:45:49",-0.49000000000000005,-0.37846153846153846]
[6,28,2018,11,45,59,-0.33,-0.33,"2018-06-28T11:45:59",-0.45,-0.38538461538461538]
[6,28,2018,11,46,9,-0.24,-0.24,"2018-06-28T11:46:09",-0.38999999999999996,-0.3888461538461539]
[6,28,2018,11,46,19,-0.27,-0.27,"2018-06-28T11:46:19",-0.34,-0.39461538461538459]
[6,28,2018,11,46,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:46:29",-0.315,-0.40038461538461539]
[6,28,2018,11,46,39,-0.33,-0.33,"2018-06-28T11:46:39",-0.3,-0.40730769230769232]
[6,28,2018,11,46,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:46:49",-0.29500000000000004,-0.41076923076923083]
[6,28,2018,11,46,59,-0.33,-0.33,{"$f":"DATE(C1209,A1209,B1209)+TIME(D1209,E1209,F1209)","v":"2018-06-28T11:46:59"},-0.29500000000000004,-0.41538461538461546]
[6,28,2018,11,47,9,-0.33,-0.33,"2018-06-28T11:47:09",-0.31000000000000005,-0.41769230769230781]
[6,28,2018,11,47,19,-0.33,-0.33,"2018-06-28T11:47:19",-0.32000000000000006,-0.41769230769230775]
[6,28,2018,11,47,29,-0.24,-0.24,"2018-06-28T11:47:29",-0.31000000000000005,-0.41423076923076929]
[6,28,2018,11,47,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:47:39",{"$f":"AVERAGE(G1208:G1213)","v":-0.28000000000000003},-0.40500000000000019]
[6,28,2018,11,47,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:47:49",-0.27999999999999997,-0.40038461538461562]
[6,28,2018,11,47,59,-0.18,-0.18,"2018-06-28T11:47:59",-0.255,-0.3911538461538463]
[6,28,2018,11,48,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:48:09",-0.25,-0.37846153846153857]
[6,28,2018,11,48,19,-0.48,-0.48,"2018-06-28T11:48:19",-0.27500000000000002,-0.37384615384615394]
[6,28,2018,11,48,29,-0.54,-0.54,"2018-06-28T11:48:29",-0.32500000000000001,-0.37269230769230777]
[6,28,2018,11,48,39,-0.51,-0.51,"2018-06-28T11:48:39",-0.38500000000000001,-0.37384615384615388]
[6,28,2018,11,48,49,-0.48,-0.48,"2018-06-28T11:48:49",-0.41499999999999998,-0.37846153846153852]
[6,28,2018,11,48,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:48:59",-0.43500000000000005,-0.37500000000000006]
[6,28,2018,11,49,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:49:09",-0.43499999999999989,-0.36461538461538479]
[6,28,2018,11,49,19,-0.27,-0.27,"2018-06-28T11:49:19",-0.39999999999999997,-0.35307692307692312]
[6,28,2018,11,49,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:49:29",-0.36000000000000004,-0.34153846153846157]
[6,28,2018,11,49,39,-0.51,-0.51,"2018-06-28T11:49:39",-0.36000000000000004,-0.33923076923076917]
[6,28,2018,11,49,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:49:49",-0.30499999999999999,-0.32769230769230767]
[6,28,2018,11,49,59,-0.18,-0.18,"2018-06-28T11:49:59",-0.28500000000000003,-0.31846153846153835]
[6,28,2018,11,50,9,-0.06,-0.06,"2018-06-28T11:50:09",-0.245,-0.30807692307692303]
[6,28,2018,11,50,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T11:50:19",-0.22500000000000001,-0.30115384615384611]
[6,28,2018,11,50,29,0,0,"2018-06-28T11:50:29",-0.17500000000000004,-0.2919230769230769]
[6,28,2018,11,50,39,0,0,"2018-06-28T11:50:39",-9.0000000000000011E-2,-0.28153846153846157]
[6,28,2018,11,50,49,-0.18,-0.18,"2018-06-28T11:50:49",-9.5000000000000015E-2,-0.27692307692307688]
[6,28,2018,11,50,59,-0.18,-0.18,"2018-06-28T11:50:59",-9.5000000000000015E-2,{"$f":"AVERAGE(G1208:G1233)","v":-0.27115384615384613}]
[6,28,2018,11,51,9,-0.27,-0.27,"2018-06-28T11:51:09",-0.13,-0.26999999999999991]
[6,28,2018,11,51,19,-0.39,-0.39,"2018-06-28T11:51:19",-0.17,-0.27230769230769225]
[6,28,2018,11,51,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T11:51:29",-0.245,-0.27692307692307688]
[6,28,2018,11,51,39,-0.39,-0.39,"2018-06-28T11:51:39",-0.31,-0.27923076923076917]
[6,28,2018,11,51,49,-0.33,-0.33,"2018-06-28T11:51:49",-0.33500000000000002,-0.28269230769230763]
[6,28,2018,11,51,59,-0.18,-0.18,"2018-06-28T11:51:59",-0.33500000000000002,-0.28384615384615375]
[6,28,2018,11,52,9,-0.12,-0.12,"2018-06-28T11:52:09",-0.31,-0.27692307692307688]
[6,28,2018,11,52,19,-0.12,-0.12,"2018-06-28T11:52:19",-0.26499999999999996,-0.27461538461538459]
[6,28,2018,11,52,29,-0.09,-0.09,"2018-06-28T11:52:29",-0.20500000000000004,-0.2665384615384615]
[6,28,2018,11,52,39,0,0,"2018-06-28T11:52:39",-0.13999999999999999,-0.24807692307692308]
[6,28,2018,11,52,49,-0.03,-0.03,"2018-06-28T11:52:49",-9.0000000000000011E-2,-0.22846153846153847]
[6,28,2018,11,52,59,-0.06,-0.06,"2018-06-28T11:52:59",-6.9999999999999993E-2,-0.21115384615384616]
[6,28,2018,11,53,9,-0.09,-0.09,"2018-06-28T11:53:09",-6.5000000000000002E-2,-0.19615384615384615]
[6,28,2018,11,53,19,-0.09,-0.09,"2018-06-28T11:53:19",-0.06,-0.18807692307692306]
[6,28,2018,11,53,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:53:29",-0.08,-0.1846153846153846]
[6,28,2018,11,53,39,-0.24,-0.24,"2018-06-28T11:53:39",-0.12,-0.18346153846153848]
[6,28,2018,11,53,49,-0.39,-0.39,"2018-06-28T11:53:49",-0.18000000000000002,-0.18692307692307694]
[6,28,2018,11,53,59,-0.36,-0.36,"2018-06-28T11:53:59",-0.22999999999999998,-0.18115384615384617]
[6,28,2018,11,54,9,-0.48,-0.48,"2018-06-28T11:54:09",-0.29499999999999998,-0.19384615384615381]
[6,28,2018,11,54,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T11:54:19",-0.35000000000000003,-0.20307692307692304]
[6,28,2018,11,54,29,-0.36,-0.36,"2018-06-28T11:54:29",-0.375,-0.2146153846153846]
[6,28,2018,11,54,39,-0.24,-0.24,"2018-06-28T11:54:39",-0.375,-0.21807692307692311]
[6,28,2018,11,54,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:54:49",-0.34500000000000003,-0.22615384615384618]
[6,28,2018,11,54,59,-0.36,-0.36,"2018-06-28T11:54:59",-0.34499999999999997,-0.24000000000000005]
[6,28,2018,11,55,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T11:55:09",-0.34,-0.25038461538461543]
[6,28,2018,11,55,19,-0.54,-0.54,"2018-06-28T11:55:19",-0.36000000000000004,-0.26423076923076921]
[6,28,2018,11,55,29,-0.48,-0.48,"2018-06-28T11:55:29",-0.38000000000000006,-0.27230769230769231]
[6,28,2018,11,55,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T11:55:39",-0.41,-0.27346153846153853]
[6,28,2018,11,55,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T11:55:49",-0.45,-0.27346153846153848]
[6,28,2018,11,55,59,-0.44999999999999996,-0.44999999999999996,"2018-06-28T11:55:59",-0.46500000000000002,-0.27576923076923077]
[6,28,2018,11,56,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T11:56:09",-0.46500000000000002,-0.2803846153846154]
[6,28,2018,11,56,19,-0.48,-0.48,"2018-06-28T11:56:19",-0.45500000000000002,-0.2919230769230769]
[6,28,2018,11,56,29,-0.48,-0.48,"2018-06-28T11:56:29",-0.45500000000000002,-0.30576923076923074]
[6,28,2018,11,56,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T11:56:39",-0.4549999999999999,-0.31730769230769229]
[6,28,2018,11,56,49,-0.57000000000000006,-0.57000000000000006,"2018-06-28T11:56:49",-0.47499999999999992,-0.33576923076923076]
[6,28,2018,11,56,59,-0.51,-0.51,"2018-06-28T11:56:59",-0.48500000000000004,-0.35538461538461541]
[6,28,2018,11,57,9,-0.39,-0.39,"2018-06-28T11:57:09",-0.47500000000000003,-0.3692307692307692]
[6,28,2018,11,57,19,-0.36,-0.36,"2018-06-28T11:57:19",-0.45500000000000002,-0.3807692307692308]
[6,28,2018,11,57,29,-0.39,-0.39,"2018-06-28T11:57:29",-0.44,-0.39230769230769236]
[6,28,2018,11,57,39,-0.33,-0.33,{"$f":"DATE(C1273,A1273,B1273)+TIME(D1273,E1273,F1273)","v":"2018-06-28T11:57:39"},-0.42500000000000004,-0.40153846153846157]
[6,28,2018,11,57,49,-0.24,-0.24,"2018-06-28T11:57:49",-0.36999999999999994,-0.40269230769230774]
[6,28,2018,11,57,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:57:59",-0.33500000000000002,-0.40500000000000003]
[6,28,2018,11,58,9,-0.18,-0.18,"2018-06-28T11:58:09",-0.3,-0.39692307692307699]
[6,28,2018,11,58,19,-0.39,-0.39,"2018-06-28T11:58:19",{"$f":"AVERAGE(G1272:G1277)","v":-0.30499999999999999},-0.39807692307692311]
[6,28,2018,11,58,29,-0.24,-0.24,"2018-06-28T11:58:29",-0.27999999999999997,-0.38884615384615395]
[6,28,2018,11,58,39,-0.18,-0.18,"2018-06-28T11:58:39",-0.25499999999999995,-0.37961538461538474]
[6,28,2018,11,58,49,-0.27,-0.27,"2018-06-28T11:58:49",-0.26,-0.37615384615384617]
[6,28,2018,11,58,59,-0.27,-0.27,"2018-06-28T11:58:59",-0.255,-0.37730769230769234]
[6,28,2018,11,59,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T11:59:09",-0.26,-0.37730769230769234]
[6,28,2018,11,59,19,-0.27,-0.27,"2018-06-28T11:59:19",-0.24,-0.37384615384615383]
[6,28,2018,11,59,29,-0.09,-0.09,"2018-06-28T11:59:29",-0.215,-0.35999999999999993]
[6,28,2018,11,59,39,-0.09,-0.09,"2018-06-28T11:59:39",-0.20000000000000004,-0.34269230769230763]
[6,28,2018,11,59,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T11:59:49",-0.20499999999999999,-0.33576923076923071]
[6,28,2018,11,59,59,-0.24,-0.24,"2018-06-28T11:59:59",-0.20000000000000004,-0.32884615384615379]
[6,28,2018,12,0,9,-0.24,-0.24,"2018-06-28T12:00:09",-0.20499999999999999,-0.3207692307692307]
[6,28,2018,12,0,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:00:19",-0.18499999999999997,-0.3092307692307692]
[6,28,2018,12,0,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:00:29",-0.20499999999999999,-0.29999999999999993]
[6,28,2018,12,0,39,-0.24,-0.24,"2018-06-28T12:00:39",-0.23,-0.29076923076923078]
[6,28,2018,12,0,49,-0.09,-0.09,"2018-06-28T12:00:49",-0.19500000000000003,-0.27576923076923077]
[6,28,2018,12,0,59,-0.18,-0.18,"2018-06-28T12:00:59",-0.18500000000000003,-0.2665384615384615]
[6,28,2018,12,1,9,-0.24,-0.24,"2018-06-28T12:01:09",-0.18500000000000003,-0.25384615384615389]
[6,28,2018,12,1,19,-0.27,-0.27,"2018-06-28T12:01:19",-0.20499999999999999,-0.24461538461538465]
[6,28,2018,12,1,29,-0.27,-0.27,"2018-06-28T12:01:29",-0.215,-0.24000000000000002]
[6,28,2018,12,1,39,-0.24,-0.24,"2018-06-28T12:01:39",-0.215,{"$f":"AVERAGE(G1272:G1297)","v":-0.23538461538461541}]
[6,28,2018,12,1,49,-0.03,-0.03,"2018-06-28T12:01:49",-0.20499999999999999,-0.22153846153846157]
[6,28,2018,12,1,59,-0.06,-0.06,"2018-06-28T12:01:59",-0.18500000000000003,-0.21115384615384608]
[6,28,2018,12,2,9,-0.06,-0.06,"2018-06-28T12:02:09",-0.15500000000000003,-0.20423076923076922]
[6,28,2018,12,2,19,0,0,"2018-06-28T12:02:19",-0.11000000000000003,-0.19269230769230766]
[6,28,2018,12,2,29,-0.06,-0.06,"2018-06-28T12:02:29",-7.4999999999999997E-2,-0.18807692307692303]
[6,28,2018,12,2,39,-0.18,-0.18,"2018-06-28T12:02:39",-6.5000000000000002E-2,-0.17999999999999997]
[6,28,2018,12,2,49,-0.51,-0.51,"2018-06-28T12:02:49",-0.14499999999999999,-0.19038461538461532]
[6,28,2018,12,2,59,-0.63,-0.63,"2018-06-28T12:02:59",-0.24,-0.20769230769230765]
[6,28,2018,12,3,9,-0.63,-0.63,"2018-06-28T12:03:09",-0.33499999999999996,-0.22153846153846152]
[6,28,2018,12,3,19,-0.81,-0.81,"2018-06-28T12:03:19",-0.47,-0.24230769230769234]
[6,28,2018,12,3,29,-0.86999999999999988,-0.86999999999999988,"2018-06-28T12:03:29",-0.60499999999999998,-0.26769230769230767]
[6,28,2018,12,3,39,-0.84000000000000008,-0.84000000000000008,"2018-06-28T12:03:39",-0.71499999999999997,-0.28961538461538461]
[6,28,2018,12,3,49,-0.57000000000000006,-0.57000000000000006,"2018-06-28T12:03:49",-0.72500000000000009,-0.30807692307692308]
[6,28,2018,12,3,59,-0.57000000000000006,-0.57000000000000006,"2018-06-28T12:03:59",-0.71499999999999997,-0.32653846153846156]
[6,28,2018,12,4,9,-0.63,-0.63,"2018-06-28T12:04:09",-0.71499999999999997,-0.33923076923076922]
[6,28,2018,12,4,19,-0.51,-0.51,"2018-06-28T12:04:19",-0.66500000000000004,-0.34961538461538461]
[6,28,2018,12,4,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:04:29",-0.54500000000000004,-0.34615384615384615]
[6,28,2018,12,4,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:04:39",-0.43,-0.3461538461538462]
[6,28,2018,12,4,49,-0.06,-0.06,"2018-06-28T12:04:49",-0.34500000000000003,-0.34038461538461545]
[6,28,2018,12,4,59,-0.36,-0.36,"2018-06-28T12:04:59",-0.31,-0.34500000000000003]
[6,28,2018,12,5,9,-0.33,-0.33,"2018-06-28T12:05:09",-0.26,-0.35423076923076924]
[6,28,2018,12,5,19,-0.57000000000000006,-0.57000000000000006,"2018-06-28T12:05:19",-0.27,-0.36923076923076931]
[6,28,2018,12,5,29,-0.54,-0.54,"2018-06-28T12:05:29",-0.33500000000000002,-0.38076923076923086]
[6,28,2018,12,5,39,-0.36,-0.36,"2018-06-28T12:05:39",-0.37000000000000005,-0.38423076923076915]
[6,28,2018,12,5,49,-0.33,-0.33,"2018-06-28T12:05:49",-0.41500000000000004,-0.3865384615384615]
[6,28,2018,12,5,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:05:59",-0.38000000000000006,-0.38307692307692309]
[6,28,2018,12,6,9,-0.24,-0.24,"2018-06-28T12:06:09",-0.36500000000000005,-0.39115384615384613]
[6,28,2018,12,6,19,-0.36,-0.36,"2018-06-28T12:06:19",-0.33,-0.40269230769230774]
[6,28,2018,12,6,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:06:29",-0.28999999999999998,-0.41192307692307689]
[6,28,2018,12,6,39,0.24,0.24,"2018-06-28T12:06:39",-0.19000000000000003,-0.40269230769230763]
[6,28,2018,12,6,49,0.44999999999999996,0.44999999999999996,"2018-06-28T12:06:49",-6.0000000000000019E-2,-0.38307692307692309]
[6,28,2018,12,6,59,0.24,0.24,"2018-06-28T12:06:59",4.9999999999999862E-3,-0.36692307692307696]
[6,28,2018,12,7,9,-0.06,-0.06,"2018-06-28T12:07:09",3.4999999999999983E-2,-0.34961538461538477]
[6,28,2018,12,7,19,-0.12,-0.12,"2018-06-28T12:07:19",7.4999999999999969E-2,-0.33000000000000007]
[6,28,2018,12,7,29,-0.36,-0.36,"2018-06-28T12:07:29",6.4999999999999988E-2,-0.31961538461538463]
[6,28,2018,12,7,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T12:07:39",-4.5000000000000019E-2,-0.30461538461538468]
[6,28,2018,12,7,49,-0.60000000000000009,-0.60000000000000009,"2018-06-28T12:07:49",-0.22,-0.29423076923076924]
[6,28,2018,12,7,59,-0.33,-0.33,"2018-06-28T12:07:59",-0.315,-0.27461538461538465]
[6,28,2018,12,8,9,-0.57000000000000006,-0.57000000000000006,"2018-06-28T12:08:09",-0.40000000000000008,-0.27461538461538465]
[6,28,2018,12,8,19,-0.60000000000000009,-0.60000000000000009,{"$f":"DATE(C1337,A1337,B1337)+TIME(D1337,E1337,F1337)","v":"2018-06-28T12:08:19"},-0.48000000000000004,-0.27576923076923077]
[6,28,2018,12,8,29,-0.51,-0.51,"2018-06-28T12:08:29",-0.505,-0.27115384615384613]
[6,28,2018,12,8,39,-0.69000000000000006,-0.69000000000000006,"2018-06-28T12:08:39",-0.55000000000000004,-0.27807692307692305]
[6,28,2018,12,8,49,-0.51,-0.51,"2018-06-28T12:08:49",-0.53500000000000003,-0.2919230769230769]
[6,28,2018,12,8,59,-0.39,-0.39,"2018-06-28T12:08:59",{"$f":"AVERAGE(G1336:G1341)","v":-0.54500000000000004},-0.30115384615384616]
[6,28,2018,12,9,9,-0.36,-0.36,"2018-06-28T12:09:09",-0.51000000000000012,-0.31269230769230766]
[6,28,2018,12,9,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T12:09:19",-0.48500000000000004,-0.31615384615384617]
[6,28,2018,12,9,29,-0.69000000000000006,-0.69000000000000006,"2018-06-28T12:09:29",-0.51500000000000001,-0.33]
[6,28,2018,12,9,39,-0.66,-0.66,"2018-06-28T12:09:39",-0.51,-0.33346153846153848]
[6,28,2018,12,9,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T12:09:49",-0.5,-0.33]
[6,28,2018,12,9,59,-0.36,-0.36,"2018-06-28T12:09:59",-0.49500000000000005,-0.33]
[6,28,2018,12,10,9,-0.36,-0.36,"2018-06-28T12:10:09",-0.49499999999999994,-0.33115384615384619]
[6,28,2018,12,10,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:10:19",-0.47000000000000003,-0.33692307692307699]
[6,28,2018,12,10,29,-0.36,-0.36,"2018-06-28T12:10:29",-0.41499999999999998,-0.34153846153846162]
[6,28,2018,12,10,39,-0.39,-0.39,"2018-06-28T12:10:39",-0.37000000000000005,-0.34269230769230774]
[6,28,2018,12,10,49,-0.36,-0.36,"2018-06-28T12:10:49",-0.35499999999999998,-0.34500000000000008]
[6,28,2018,12,10,59,-0.18,-0.18,"2018-06-28T12:10:59",-0.32500000000000001,-0.36115384615384616]
[6,28,2018,12,11,9,-0.27,-0.27,"2018-06-28T12:11:09",-0.31,-0.3888461538461539]
[6,28,2018,12,11,19,-0.27,-0.27,"2018-06-28T12:11:19",-0.30499999999999999,-0.40846153846153843]
[6,28,2018,12,11,29,-0.12,-0.12,"2018-06-28T12:11:29",-0.26499999999999996,-0.41076923076923078]
[6,28,2018,12,11,39,-0.03,-0.03,"2018-06-28T12:11:39",-0.20500000000000004,-0.40730769230769232]
[6,28,2018,12,11,49,-0.36,-0.36,"2018-06-28T12:11:49",-0.20499999999999999,-0.40730769230769226]
[6,28,2018,12,11,59,-0.63,-0.63,"2018-06-28T12:11:59",-0.28000000000000003,-0.41538461538461535]
[6,28,2018,12,12,9,-0.24,-0.24,"2018-06-28T12:12:09",-0.27500000000000002,-0.40153846153846151]
[6,28,2018,12,12,19,-0.27,-0.27,"2018-06-28T12:12:19",-0.27500000000000002,{"$f":"AVERAGE(G1336:G1361)","v":-0.39923076923076917}]
[6,28,2018,12,12,29,-0.27,-0.27,"2018-06-28T12:12:29",-0.3,-0.38769230769230767]
[6,28,2018,12,12,39,-0.18,-0.18,"2018-06-28T12:12:39",-0.32500000000000001,-0.37153846153846154]
[6,28,2018,12,12,49,-0.09,-0.09,"2018-06-28T12:12:49",-0.28000000000000003,-0.35538461538461541]
[6,28,2018,12,12,59,-0.06,-0.06,"2018-06-28T12:12:59",-0.18500000000000003,-0.33115384615384613]
[6,28,2018,12,13,9,-0.03,-0.03,"2018-06-28T12:13:09",-0.15,-0.31269230769230766]
[6,28,2018,12,13,19,-0.27,-0.27,"2018-06-28T12:13:19",-0.15000000000000002,-0.30807692307692303]
[6,28,2018,12,13,29,-0.48,-0.48,"2018-06-28T12:13:29",-0.18499999999999997,-0.31269230769230766]
[6,28,2018,12,13,39,-0.48,-0.48,"2018-06-28T12:13:39",-0.23499999999999999,-0.31384615384615383]
[6,28,2018,12,13,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:13:49",-0.26999999999999996,-0.29884615384615387]
[6,28,2018,12,13,59,-0.18,-0.18,"2018-06-28T12:13:59",-0.28999999999999998,-0.2803846153846154]
[6,28,2018,12,14,9,-0.06,-0.06,"2018-06-28T12:14:09",-0.29499999999999998,-0.26538461538461533]
[6,28,2018,12,14,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:14:19",-0.28499999999999998,-0.25961538461538453]
[6,28,2018,12,14,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T12:14:29",-0.27999999999999997,-0.2630769230769231]
[6,28,2018,12,14,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T12:14:39",-0.27,-0.26769230769230773]
[6,28,2018,12,14,49,-0.48,-0.48,"2018-06-28T12:14:49",-0.3,-0.27230769230769231]
[6,28,2018,12,14,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T12:14:59",-0.34,-0.27346153846153842]
[6,28,2018,12,15,9,-0.54,-0.54,"2018-06-28T12:15:09",-0.42,-0.28038461538461534]
[6,28,2018,12,15,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T12:15:19",-0.45500000000000002,-0.28961538461538461]
[6,28,2018,12,15,29,-0.39,-0.39,"2018-06-28T12:15:29",-0.44500000000000006,-0.29423076923076918]
[6,28,2018,12,15,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:15:39",-0.42499999999999999,-0.29538461538461536]
[6,28,2018,12,15,49,-0.57000000000000006,-0.57000000000000006,"2018-06-28T12:15:49",-0.44000000000000011,-0.31269230769230766]
[6,28,2018,12,15,59,-0.48,-0.48,"2018-06-28T12:15:59",-0.45,-0.33]
[6,28,2018,12,16,9,-0.33,-0.33,"2018-06-28T12:16:09",-0.41500000000000004,-0.32884615384615379]
[6,28,2018,12,16,19,-0.36,-0.36,"2018-06-28T12:16:19",-0.40500000000000003,-0.31846153846153846]
[6,28,2018,12,16,29,-0.51,-0.51,"2018-06-28T12:16:29",-0.42499999999999999,-0.32884615384615379]
[6,28,2018,12,16,39,-0.54,-0.54,"2018-06-28T12:16:39",-0.46500000000000002,-0.33923076923076922]
[6,28,2018,12,16,49,-0.54,-0.54,"2018-06-28T12:16:49",-0.45999999999999996,-0.34961538461538461]
[6,28,2018,12,16,59,-0.48,-0.48,"2018-06-28T12:16:59",-0.46,-0.36115384615384616]
[6,28,2018,12,17,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T12:17:09",-0.47500000000000003,-0.37384615384615388]
[6,28,2018,12,17,19,-0.36,-0.36,"2018-06-28T12:17:19",-0.47500000000000003,-0.38538461538461544]
[6,28,2018,12,17,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:17:29",-0.43999999999999995,-0.39576923076923082]
[6,28,2018,12,17,39,-0.27,-0.27,"2018-06-28T12:17:39",-0.39499999999999996,-0.39576923076923082]
[6,28,2018,12,17,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:17:49",-0.34,-0.38538461538461538]
[6,28,2018,12,17,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:17:59",-0.31,-0.37846153846153852]
[6,28,2018,12,18,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:18:09",-0.29000000000000004,-0.37846153846153852]
[6,28,2018,12,18,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:18:19",-0.28000000000000003,-0.3830769230769232]
[6,28,2018,12,18,29,-0.39,-0.39,"2018-06-28T12:18:29",-0.29499999999999998,-0.39576923076923087]
[6,28,2018,12,18,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T12:18:39",-0.32,-0.40384615384615397]
[6,28,2018,12,18,49,-0.36,-0.36,"2018-06-28T12:18:49",-0.34499999999999997,-0.40038461538461551]
[6,28,2018,12,18,59,-0.24,-0.24,{"$f":"DATE(C1401,A1401,B1401)+TIME(D1401,E1401,F1401)","v":"2018-06-28T12:18:59"},-0.33499999999999996,-0.39346153846153847]
[6,28,2018,12,19,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:19:09",-0.33500000000000002,-0.38653846153846161]
[6,28,2018,12,19,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:19:19",-0.33499999999999996,-0.38192307692307698]
[6,28,2018,12,19,29,-0.36,-0.36,"2018-06-28T12:19:29",-0.33,-0.375]
[6,28,2018,12,19,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T12:19:39",{"$f":"AVERAGE(G1400:G1405)","v":-0.33},-0.375]
[6,28,2018,12,19,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T12:19:49",-0.34500000000000003,-0.37730769230769223]
[6,28,2018,12,19,59,-0.36,-0.36,"2018-06-28T12:19:59",-0.36499999999999999,-0.37961538461538452]
[6,28,2018,12,20,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:20:09",-0.36500000000000005,-0.36923076923076914]
[6,28,2018,12,20,19,-0.27,-0.27,"2018-06-28T12:20:19",-0.36000000000000004,-0.3611538461538461]
[6,28,2018,12,20,29,-0.33,-0.33,"2018-06-28T12:20:29",-0.35499999999999998,-0.3611538461538461]
[6,28,2018,12,20,39,-0.33,-0.33,"2018-06-28T12:20:39",-0.34,-0.36000000000000004]
[6,28,2018,12,20,49,-0.39,-0.39,"2018-06-28T12:20:49",-0.33,-0.35538461538461541]
[6,28,2018,12,20,59,-0.39,-0.39,"2018-06-28T12:20:59",-0.33500000000000002,-0.34961538461538466]
[6,28,2018,12,21,9,-0.54,-0.54,"2018-06-28T12:21:09",-0.37500000000000006,-0.34961538461538461]
[6,28,2018,12,21,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T12:21:19",-0.40499999999999997,-0.34846153846153843]
[6,28,2018,12,21,29,-0.33,-0.33,"2018-06-28T12:21:29",-0.40499999999999997,-0.34500000000000003]
[6,28,2018,12,21,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T12:21:39",-0.42,-0.34730769230769226]
[6,28,2018,12,21,49,-0.36,-0.36,"2018-06-28T12:21:49",-0.41499999999999998,-0.34961538461538461]
[6,28,2018,12,21,59,-0.44999999999999996,-0.44999999999999996,"2018-06-28T12:21:59",-0.42499999999999999,-0.35653846153846147]
[6,28,2018,12,22,9,-0.12,-0.12,"2018-06-28T12:22:09",-0.35499999999999998,-0.35307692307692295]
[6,28,2018,12,22,19,-0.18,-0.18,"2018-06-28T12:22:19",-0.30999999999999994,-0.34846153846153832]
[6,28,2018,12,22,29,-0.33,-0.33,"2018-06-28T12:22:29",-0.31,-0.34961538461538455]
[6,28,2018,12,22,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:22:39",-0.27499999999999997,-0.34615384615384615]
[6,28,2018,12,22,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:22:49",-0.24,-0.33692307692307699]
[6,28,2018,12,22,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:22:59",-0.20000000000000004,{"$f":"AVERAGE(G1400:G1425)","v":-0.3288461538461539}]
[6,28,2018,12,23,9,-0.06,-0.06,"2018-06-28T12:23:09",-0.19000000000000003,-0.3173076923076924]
[6,28,2018,12,23,19,-0.09,-0.09,"2018-06-28T12:23:19",-0.17500000000000004,-0.3115384615384616]
[6,28,2018,12,23,29,-0.18,-0.18,"2018-06-28T12:23:29",-0.15000000000000002,-0.30692307692307697]
[6,28,2018,12,23,39,-0.09,-0.09,"2018-06-28T12:23:39",-0.12999999999999998,-0.29884615384615387]
[6,28,2018,12,23,49,-0.18,-0.18,"2018-06-28T12:23:49",-0.13500000000000001,-0.2919230769230769]
[6,28,2018,12,23,59,-0.18,-0.18,"2018-06-28T12:23:59",-0.12999999999999998,-0.28269230769230769]
[6,28,2018,12,24,9,-0.18,-0.18,"2018-06-28T12:24:09",-0.15,-0.27230769230769225]
[6,28,2018,12,24,19,-0.03,-0.03,"2018-06-28T12:24:19",-0.14000000000000001,-0.25961538461538458]
[6,28,2018,12,24,29,-0.09,-0.09,"2018-06-28T12:24:29",-0.125,-0.25153846153846149]
[6,28,2018,12,24,39,-0.12,-0.12,"2018-06-28T12:24:39",-0.13,-0.24576923076923068]
[6,28,2018,12,24,49,0,0,"2018-06-28T12:24:49",-9.9999999999999992E-2,-0.23307692307692299]
[6,28,2018,12,24,59,0.09,0.09,"2018-06-28T12:24:59",-5.4999999999999993E-2,-0.21692307692307691]
[6,28,2018,12,25,9,-0.09,-0.09,"2018-06-28T12:25:09",-0.04,-0.2053846153846153]
[6,28,2018,12,25,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:25:19",-0.06,-0.19615384615384615]
[6,28,2018,12,25,29,-0.12,-0.12,"2018-06-28T12:25:29",-6.5000000000000002E-2,-0.18000000000000002]
[6,28,2018,12,25,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:25:39",-7.0000000000000007E-2,-0.16846153846153847]
[6,28,2018,12,25,49,-0.06,-0.06,"2018-06-28T12:25:49",-0.08,-0.15807692307692309]
[6,28,2018,12,25,59,-0.09,-0.09,"2018-06-28T12:25:59",-0.11,-0.14538461538461539]
[6,28,2018,12,26,9,-0.06,-0.06,"2018-06-28T12:26:09",-0.10500000000000002,-0.13384615384615384]
[6,28,2018,12,26,19,-0.06,-0.06,"2018-06-28T12:26:19",-9.0000000000000011E-2,-0.11884615384615384]
[6,28,2018,12,26,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:26:29",-0.10500000000000002,-0.1223076923076923]
[6,28,2018,12,26,39,-0.33,-0.33,"2018-06-28T12:26:39",-0.13500000000000001,-0.12807692307692309]
[6,28,2018,12,26,49,-0.18,-0.18,"2018-06-28T12:26:49",-0.155,-0.12230769230769231]
[6,28,2018,12,26,59,0,0,"2018-06-28T12:26:59",-0.14000000000000001,-0.11423076923076923]
[6,28,2018,12,27,9,-0.03,-0.03,"2018-06-28T12:27:09",-0.13500000000000001,-0.10961538461538461]
[6,28,2018,12,27,19,-0.03,-0.03,"2018-06-28T12:27:19",-0.13,-0.10269230769230769]
[6,28,2018,12,27,29,-0.27,-0.27,"2018-06-28T12:27:29",-0.14000000000000001,-0.11076923076923079]
[6,28,2018,12,27,39,0.03,0.03,"2018-06-28T12:27:39",-0.08,-0.10615384615384617]
[6,28,2018,12,27,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:27:49",-7.5000000000000011E-2,-0.105]
[6,28,2018,12,27,59,-0.09,-0.09,"2018-06-28T12:27:59",-9.0000000000000011E-2,-0.105]
[6,28,2018,12,28,9,-0.06,-0.06,"2018-06-28T12:28:09",-9.5000000000000015E-2,-0.10038461538461538]
[6,28,2018,12,28,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:28:19",-0.115,-9.9230769230769234E-2]
[6,28,2018,12,28,29,-0.18,-0.18,"2018-06-28T12:28:29",-0.10000000000000002,-9.9230769230769234E-2]
[6,28,2018,12,28,39,0.03,0.03,"2018-06-28T12:28:39",-0.10000000000000002,-9.6923076923076917E-2]
[6,28,2018,12,28,49,0.03,0.03,"2018-06-28T12:28:49",-7.0000000000000007E-2,-9.2307692307692327E-2]
[6,28,2018,12,28,59,-0.09,-0.09,"2018-06-28T12:28:59",-6.9999999999999993E-2,-9.1153846153846169E-2]
[6,28,2018,12,29,9,-0.12,-0.12,"2018-06-28T12:29:09",-0.08,-9.5769230769230801E-2]
[6,28,2018,12,29,19,-0.03,-0.03,"2018-06-28T12:29:19",-0.06,-0.10038461538461539]
[6,28,2018,12,29,29,-0.09,-0.09,"2018-06-28T12:29:29",-4.5000000000000005E-2,-0.10038461538461539]
[6,28,2018,12,29,39,-0.18,-0.18,{"$f":"DATE(C1465,A1465,B1465)+TIME(D1465,E1465,F1465)","v":"2018-06-28T12:29:39"},-0.08,-0.10153846153846156]
[6,28,2018,12,29,49,-0.18,-0.18,"2018-06-28T12:29:49",-0.11499999999999999,-0.10384615384615389]
[6,28,2018,12,29,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:29:59",-0.13500000000000001,-0.10615384615384617]
[6,28,2018,12,30,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:30:09",-0.16500000000000001,-0.11538461538461539]
[6,28,2018,12,30,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T12:30:19",{"$f":"AVERAGE(G1464:G1469)","v":-0.23},-0.12807692307692312]
[6,28,2018,12,30,29,-0.27,-0.27,"2018-06-28T12:30:29",-0.26,-0.13615384615384618]
[6,28,2018,12,30,39,-0.24,-0.24,"2018-06-28T12:30:39",-0.27,-0.1430769230769231]
[6,28,2018,12,30,49,-0.18,-0.18,"2018-06-28T12:30:49",-0.27,-0.14192307692307693]
[6,28,2018,12,30,59,-0.27,-0.27,"2018-06-28T12:30:59",-0.27999999999999997,-0.13961538461538461]
[6,28,2018,12,31,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:31:09",-0.26500000000000001,-0.14076923076923079]
[6,28,2018,12,31,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:31:19",-0.21999999999999997,-0.14653846153846153]
[6,28,2018,12,31,29,0,0,"2018-06-28T12:31:29",-0.17499999999999996,-0.14538461538461539]
[6,28,2018,12,31,39,-0.06,-0.06,"2018-06-28T12:31:39",-0.14500000000000002,-0.14653846153846153]
[6,28,2018,12,31,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:31:49",-0.16500000000000004,-0.14769230769230768]
[6,28,2018,12,31,59,-0.18,-0.18,"2018-06-28T12:31:59",-0.15000000000000002,-0.15576923076923077]
[6,28,2018,12,32,9,-0.24,-0.24,"2018-06-28T12:32:09",-0.155,-0.15923076923076923]
[6,28,2018,12,32,19,-0.24,-0.24,"2018-06-28T12:32:19",-0.17,-0.16500000000000001]
[6,28,2018,12,32,29,-0.36,-0.36,"2018-06-28T12:32:29",-0.22999999999999998,-0.17653846153846156]
[6,28,2018,12,32,39,-0.27,-0.27,"2018-06-28T12:32:39",-0.26499999999999996,-0.18115384615384619]
[6,28,2018,12,32,49,-0.27,-0.27,"2018-06-28T12:32:49",-0.26,-0.18461538461538465]
[6,28,2018,12,32,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:32:59",-0.25499999999999995,-0.19153846153846155]
[6,28,2018,12,33,9,-0.24,-0.24,"2018-06-28T12:33:09",-0.255,-0.20192307692307693]
[6,28,2018,12,33,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:33:19",-0.25,-0.20653846153846153]
[6,28,2018,12,33,29,-0.24,-0.24,"2018-06-28T12:33:29",-0.23,-0.21115384615384619]
[6,28,2018,12,33,39,-0.33,-0.33,"2018-06-28T12:33:39",-0.24000000000000002,{"$f":"AVERAGE(G1464:G1489)","v":-0.22269230769230777}]
[6,28,2018,12,33,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:33:49",-0.23,-0.22730769230769232]
[6,28,2018,12,33,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:33:59",-0.255,-0.23192307692307693]
[6,28,2018,12,34,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:34:09",-0.26500000000000001,-0.23653846153846156]
[6,28,2018,12,34,19,-0.39,-0.39,"2018-06-28T12:34:19",-0.29499999999999998,-0.24346153846153845]
[6,28,2018,12,34,29,-0.39,-0.39,"2018-06-28T12:34:29",-0.32000000000000006,-0.24692307692307691]
[6,28,2018,12,34,39,-0.39,-0.39,"2018-06-28T12:34:39",-0.33000000000000007,-0.24576923076923071]
[6,28,2018,12,34,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:34:49",-0.34500000000000003,-0.24692307692307686]
[6,28,2018,12,34,59,-0.33,-0.33,"2018-06-28T12:34:59",-0.35000000000000003,-0.25038461538461532]
[6,28,2018,12,35,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:35:09",-0.33500000000000002,-0.25153846153846149]
[6,28,2018,12,35,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:35:19",-0.30499999999999999,-0.24923076923076917]
[6,28,2018,12,35,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:35:29",-0.27499999999999997,-0.24923076923076917]
[6,28,2018,12,35,39,-0.24,-0.24,"2018-06-28T12:35:39",-0.25,-0.25269230769230766]
[6,28,2018,12,35,49,-0.33,-0.33,"2018-06-28T12:35:49",-0.255,-0.26538461538461533]
[6,28,2018,12,35,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T12:35:59",-0.27,-0.27923076923076917]
[6,28,2018,12,36,9,-0.39,-0.39,"2018-06-28T12:36:09",-0.30000000000000004,-0.28269230769230769]
[6,28,2018,12,36,19,-0.36,-0.36,"2018-06-28T12:36:19",-0.32500000000000001,-0.28961538461538461]
[6,28,2018,12,36,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:36:29",-0.34,-0.2919230769230769]
[6,28,2018,12,36,39,-0.24,-0.24,"2018-06-28T12:36:39",-0.34,-0.2919230769230769]
[6,28,2018,12,36,49,-0.39,-0.39,"2018-06-28T12:36:49",-0.35000000000000003,-0.29307692307692312]
[6,28,2018,12,36,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T12:36:59",-0.35000000000000003,-0.29884615384615387]
[6,28,2018,12,37,9,-0.39,-0.39,"2018-06-28T12:37:09",-0.35000000000000003,-0.30346153846153845]
[6,28,2018,12,37,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:37:19",-0.34,-0.30923076923076925]
[6,28,2018,12,37,29,-0.27,-0.27,"2018-06-28T12:37:29",-0.33499999999999996,-0.31038461538461537]
[6,28,2018,12,37,39,-0.33,-0.33,"2018-06-28T12:37:39",-0.35000000000000003,-0.315]
[6,28,2018,12,37,49,-0.18,-0.18,"2018-06-28T12:37:49",-0.315,-0.31269230769230766]
[6,28,2018,12,37,59,-0.18,-0.18,"2018-06-28T12:37:59",-0.27499999999999997,-0.30692307692307685]
[6,28,2018,12,38,9,-0.09,-0.09,"2018-06-28T12:38:09",-0.22500000000000001,-0.30230769230769228]
[6,28,2018,12,38,19,-0.03,-0.03,"2018-06-28T12:38:19",-0.18000000000000002,-0.2919230769230769]
[6,28,2018,12,38,29,-0.03,-0.03,"2018-06-28T12:38:29",-0.13999999999999999,-0.28153846153846146]
[6,28,2018,12,38,39,-0.06,-0.06,"2018-06-28T12:38:39",-9.5000000000000015E-2,-0.26884615384615385]
[6,28,2018,12,38,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:38:49",-0.11500000000000003,-0.26538461538461533]
[6,28,2018,12,38,59,-0.36,-0.36,"2018-06-28T12:38:59",-0.14499999999999999,-0.26423076923076921]
[6,28,2018,12,39,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T12:39:09",-0.20000000000000004,-0.26884615384615385]
[6,28,2018,12,39,19,-0.27,-0.27,"2018-06-28T12:39:19",-0.24,-0.2665384615384615]
[6,28,2018,12,39,29,-0.36,-0.36,"2018-06-28T12:39:29",-0.29499999999999998,-0.27230769230769236]
[6,28,2018,12,39,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T12:39:39",-0.35499999999999998,-0.2803846153846154]
[6,28,2018,12,39,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:39:49",-0.34,-0.2803846153846154]
[6,28,2018,12,39,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:39:59",-0.315,-0.27923076923076917]
[6,28,2018,12,40,9,-0.12,-0.12,"2018-06-28T12:40:09",-0.26499999999999996,-0.27115384615384619]
[6,28,2018,12,40,19,0,0,{"$f":"DATE(C1529,A1529,B1529)+TIME(D1529,E1529,F1529)","v":"2018-06-28T12:40:19"},-0.21999999999999997,-0.255]
[6,28,2018,12,40,29,0.09,0.09,"2018-06-28T12:40:29",-0.14500000000000002,-0.23653846153846156]
[6,28,2018,12,40,39,-0.03,-0.03,"2018-06-28T12:40:39",-8.0000000000000016E-2,-0.22384615384615389]
[6,28,2018,12,40,49,0.06,0.06,"2018-06-28T12:40:49",-3.5000000000000003E-2,-0.21000000000000002]
[6,28,2018,12,40,59,-0.12,-0.12,"2018-06-28T12:40:59",{"$f":"AVERAGE(G1528:G1533)","v":-0.02},-0.20538461538461542]
[6,28,2018,12,41,9,-0.24,-0.24,"2018-06-28T12:41:09",-0.04,-0.19961538461538467]
[6,28,2018,12,41,19,-0.36,-0.36,"2018-06-28T12:41:19",-9.9999999999999992E-2,-0.19730769230769238]
[6,28,2018,12,41,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:41:29",-0.13999999999999999,-0.18807692307692317]
[6,28,2018,12,41,39,-0.09,-0.09,"2018-06-28T12:41:39",-0.15,-0.18000000000000002]
[6,28,2018,12,41,49,-0.24,-0.24,"2018-06-28T12:41:49",-0.19999999999999998,-0.17884615384615385]
[6,28,2018,12,41,59,-0.18,-0.18,"2018-06-28T12:41:59",-0.21,-0.17307692307692304]
[6,28,2018,12,42,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:42:09",-0.20499999999999999,-0.17423076923076922]
[6,28,2018,12,42,19,-0.27,-0.27,"2018-06-28T12:42:19",-0.18999999999999997,-0.17769230769230765]
[6,28,2018,12,42,29,-0.18,-0.18,"2018-06-28T12:42:29",-0.19499999999999998,-0.18115384615384611]
[6,28,2018,12,42,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:42:39",-0.215,-0.18807692307692306]
[6,28,2018,12,42,49,-0.03,-0.03,"2018-06-28T12:42:49",-0.18000000000000002,-0.18807692307692309]
[6,28,2018,12,42,59,-0.06,-0.06,"2018-06-28T12:42:59",-0.16000000000000003,-0.18807692307692306]
[6,28,2018,12,43,9,-0.06,-0.06,"2018-06-28T12:43:09",-0.13500000000000001,-0.17884615384615382]
[6,28,2018,12,43,19,-0.18,-0.18,"2018-06-28T12:43:19",-0.12,-0.1719230769230769]
[6,28,2018,12,43,29,-0.09,-0.09,"2018-06-28T12:43:29",-0.105,-0.15923076923076923]
[6,28,2018,12,43,39,-0.09,-0.09,"2018-06-28T12:43:39",-8.4999999999999978E-2,-0.15230769230769228]
[6,28,2018,12,43,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:43:49",-0.105,-0.14423076923076922]
[6,28,2018,12,43,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:43:59",-0.12,-0.13384615384615384]
[6,28,2018,12,44,9,-0.18,-0.18,"2018-06-28T12:44:09",-0.14000000000000001,-0.13269230769230769]
[6,28,2018,12,44,19,-0.39,-0.39,"2018-06-28T12:44:19",-0.17500000000000002,{"$f":"AVERAGE(G1528:G1553)","v":-0.13961538461538461}]
[6,28,2018,12,44,29,-0.48,-0.48,"2018-06-28T12:44:29",-0.24,-0.15346153846153845]
[6,28,2018,12,44,39,-0.44999999999999996,-0.44999999999999996,"2018-06-28T12:44:39",-0.3,-0.17076923076923076]
[6,28,2018,12,44,49,-0.36,-0.36,"2018-06-28T12:44:49",-0.33499999999999996,-0.18807692307692309]
[6,28,2018,12,44,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:44:59",-0.36000000000000004,-0.19846153846153847]
[6,28,2018,12,45,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:45:09",-0.35499999999999998,-0.20653846153846153]
[6,28,2018,12,45,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:45:19",-0.32500000000000001,-0.21]
[6,28,2018,12,45,29,-0.06,-0.06,"2018-06-28T12:45:29",-0.25499999999999995,-0.2030769230769231]
[6,28,2018,12,45,39,-0.06,-0.06,"2018-06-28T12:45:39",-0.19000000000000003,-0.19153846153846152]
[6,28,2018,12,45,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:45:49",-0.16500000000000004,-0.19384615384615383]
[6,28,2018,12,45,59,-0.18,-0.18,"2018-06-28T12:45:59",-0.14500000000000002,-0.1973076923076923]
[6,28,2018,12,46,9,-0.18,-0.18,"2018-06-28T12:46:09",-0.15,-0.19499999999999998]
[6,28,2018,12,46,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:46:19",-0.15,-0.1961538461538461]
[6,28,2018,12,46,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:46:29",-0.17500000000000002,-0.1961538461538461]
[6,28,2018,12,46,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:46:39",-0.215,-0.19730769230769227]
[6,28,2018,12,46,49,-0.18,-0.18,"2018-06-28T12:46:49",-0.21,-0.19730769230769227]
[6,28,2018,12,46,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:46:59",-0.20499999999999999,-0.19499999999999998]
[6,28,2018,12,47,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:47:09",-0.21000000000000005,-0.20192307692307696]
[6,28,2018,12,47,19,-0.18,-0.18,"2018-06-28T12:47:19",-0.20499999999999999,-0.20653846153846153]
[6,28,2018,12,47,29,-0.09,-0.09,"2018-06-28T12:47:29",-0.18500000000000003,-0.2076923076923077]
[6,28,2018,12,47,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:47:39",-0.17,-0.20884615384615385]
[6,28,2018,12,47,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:47:49",-0.19000000000000003,-0.21692307692307691]
[6,28,2018,12,47,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:47:59",-0.19999999999999998,-0.22153846153846152]
[6,28,2018,12,48,9,-0.09,-0.09,"2018-06-28T12:48:09",-0.18000000000000002,-0.2192307692307692]
[6,28,2018,12,48,19,-0.06,-0.06,"2018-06-28T12:48:19",-0.16,-0.21576923076923074]
[6,28,2018,12,48,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:48:29",-0.17,-0.2146153846153846]
[6,28,2018,12,48,39,-0.12,-0.12,"2018-06-28T12:48:39",-0.155,-0.20423076923076922]
[6,28,2018,12,48,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:48:49",-0.13,-0.19153846153846155]
[6,28,2018,12,48,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:48:59",-0.13,-0.18230769230769231]
[6,28,2018,12,49,9,-0.18,-0.18,"2018-06-28T12:49:09",-0.14500000000000002,-0.17538461538461542]
[6,28,2018,12,49,19,-0.18,-0.18,"2018-06-28T12:49:19",-0.16500000000000001,-0.17076923076923076]
[6,28,2018,12,49,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:49:29",-0.16500000000000001,-0.17076923076923076]
[6,28,2018,12,49,39,-0.12,-0.12,"2018-06-28T12:49:39",-0.16500000000000001,-0.1673076923076923]
[6,28,2018,12,49,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:49:49",-0.19000000000000003,-0.17653846153846153]
[6,28,2018,12,49,59,-0.36,-0.36,"2018-06-28T12:49:59",-0.215,-0.18807692307692309]
[6,28,2018,12,50,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:50:09",-0.23499999999999999,-0.19153846153846155]
[6,28,2018,12,50,19,-0.39,-0.39,"2018-06-28T12:50:19",-0.27,-0.19961538461538458]
[6,28,2018,12,50,29,-0.33,-0.33,"2018-06-28T12:50:29",-0.30000000000000004,-0.20538461538461539]
[6,28,2018,12,50,39,-0.27,-0.27,"2018-06-28T12:50:39",-0.32500000000000001,-0.2076923076923077]
[6,28,2018,12,50,49,-0.09,-0.09,"2018-06-28T12:50:49",-0.29000000000000004,-0.20307692307692313]
[6,28,2018,12,50,59,-0.12,-0.12,{"$f":"DATE(C1593,A1593,B1593)+TIME(D1593,E1593,F1593)","v":"2018-06-28T12:50:59"},-0.25,-0.19615384615384618]
[6,28,2018,12,51,9,-0.12,-0.12,"2018-06-28T12:51:09",-0.22000000000000006,-0.19384615384615389]
[6,28,2018,12,51,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:51:19",-0.18000000000000002,-0.19384615384615389]
[6,28,2018,12,51,29,-0.09,-0.09,"2018-06-28T12:51:29",-0.13999999999999999,-0.18923076923076923]
[6,28,2018,12,51,39,-0.12,-0.12,"2018-06-28T12:51:39",{"$f":"AVERAGE(G1592:G1597)","v":-0.11499999999999999},-0.18692307692307694]
[6,28,2018,12,51,49,-0.06,-0.06,"2018-06-28T12:51:49",-0.10999999999999999,-0.18576923076923077]
[6,28,2018,12,51,59,-0.18,-0.18,"2018-06-28T12:51:59",-0.12,-0.1846153846153846]
[6,28,2018,12,52,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:52:09",-0.13500000000000001,-0.18115384615384617]
[6,28,2018,12,52,19,-0.24,-0.24,"2018-06-28T12:52:19",-0.15,-0.18230769230769228]
[6,28,2018,12,52,29,-0.24,-0.24,"2018-06-28T12:52:29",-0.17500000000000002,-0.18807692307692309]
[6,28,2018,12,52,39,-0.24,-0.24,"2018-06-28T12:52:39",-0.19499999999999998,-0.19500000000000003]
[6,28,2018,12,52,49,-0.18,-0.18,"2018-06-28T12:52:49",-0.21499999999999997,-0.19615384615384621]
[6,28,2018,12,52,59,-0.12,-0.12,"2018-06-28T12:52:59",-0.20499999999999999,-0.19615384615384618]
[6,28,2018,12,53,9,-0.12,-0.12,"2018-06-28T12:53:09",-0.19000000000000003,-0.19500000000000001]
[6,28,2018,12,53,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:53:19",-0.17499999999999996,-0.19269230769230772]
[6,28,2018,12,53,29,-0.18,-0.18,"2018-06-28T12:53:29",-0.16500000000000001,-0.19269230769230772]
[6,28,2018,12,53,39,-0.27,-0.27,"2018-06-28T12:53:39",-0.17,-0.19615384615384621]
[6,28,2018,12,53,49,-0.33,-0.33,"2018-06-28T12:53:49",-0.19500000000000003,-0.20307692307692313]
[6,28,2018,12,53,59,-0.27,-0.27,"2018-06-28T12:53:59",-0.22,-0.20884615384615385]
[6,28,2018,12,54,9,-0.27,-0.27,"2018-06-28T12:54:09",-0.24500000000000002,-0.2076923076923077]
[6,28,2018,12,54,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:54:19",-0.27,-0.20538461538461542]
[6,28,2018,12,54,29,-0.33,-0.33,"2018-06-28T12:54:29",-0.29500000000000004,-0.20653846153846153]
[6,28,2018,12,54,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:54:39",-0.30000000000000004,-0.20307692307692304]
[6,28,2018,12,54,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:54:49",-0.28000000000000003,-0.19846153846153847]
[6,28,2018,12,54,59,-0.18,-0.18,"2018-06-28T12:54:59",-0.26500000000000001,{"$f":"AVERAGE(G1592:G1617)","v":-0.19500000000000001}]
[6,28,2018,12,55,9,-0.18,-0.18,"2018-06-28T12:55:09",-0.25,-0.19846153846153844]
[6,28,2018,12,55,19,-0.18,-0.18,"2018-06-28T12:55:19",-0.22999999999999998,-0.20076923076923073]
[6,28,2018,12,55,29,-0.09,-0.09,"2018-06-28T12:55:29",-0.18999999999999997,-0.19961538461538458]
[6,28,2018,12,55,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:55:39",-0.16500000000000001,-0.19961538461538458]
[6,28,2018,12,55,49,-0.36,-0.36,"2018-06-28T12:55:49",-0.19000000000000003,-0.21]
[6,28,2018,12,55,59,-0.48,-0.48,"2018-06-28T12:55:59",-0.24,-0.22384615384615378]
[6,28,2018,12,56,9,-0.54,-0.54,"2018-06-28T12:56:09",-0.3,-0.24230769230769231]
[6,28,2018,12,56,19,-0.51,-0.51,"2018-06-28T12:56:19",-0.35499999999999998,-0.255]
[6,28,2018,12,56,29,-0.57000000000000006,-0.57000000000000006,"2018-06-28T12:56:29",-0.43500000000000005,-0.2688461538461539]
[6,28,2018,12,56,39,-0.51,-0.51,"2018-06-28T12:56:39",-0.49499999999999994,-0.27923076923076928]
[6,28,2018,12,56,49,-0.27,-0.27,"2018-06-28T12:56:49",-0.48000000000000004,-0.2803846153846154]
[6,28,2018,12,56,59,-0.33,-0.33,"2018-06-28T12:56:59",-0.45500000000000002,-0.28384615384615386]
[6,28,2018,12,57,9,-0.33,-0.33,"2018-06-28T12:57:09",-0.42,-0.28961538461538466]
[6,28,2018,12,57,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:57:19",-0.38500000000000006,-0.29653846153846153]
[6,28,2018,12,57,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:57:29",-0.34,-0.3034615384615385]
[6,28,2018,12,57,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:57:39",-0.30500000000000005,-0.30923076923076925]
[6,28,2018,12,57,49,-0.27,-0.27,"2018-06-28T12:57:49",-0.30500000000000005,-0.31269230769230771]
[6,28,2018,12,57,59,-0.27,-0.27,"2018-06-28T12:57:59",-0.29500000000000004,-0.31269230769230766]
[6,28,2018,12,58,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T12:58:09",-0.29000000000000004,-0.31153846153846154]
[6,28,2018,12,58,19,-0.24,-0.24,"2018-06-28T12:58:19",-0.28000000000000003,-0.31038461538461531]
[6,28,2018,12,58,29,-0.24,-0.24,"2018-06-28T12:58:29",-0.27,-0.3092307692307692]
[6,28,2018,12,58,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:58:39",-0.255,-0.30576923076923074]
[6,28,2018,12,58,49,-0.24,-0.24,"2018-06-28T12:58:49",-0.25,-0.30230769230769228]
[6,28,2018,12,58,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:58:59",-0.24,-0.29884615384615387]
[6,28,2018,12,59,9,-0.24,-0.24,"2018-06-28T12:59:09",-0.22999999999999998,-0.3]
[6,28,2018,12,59,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:59:19",-0.22499999999999998,-0.30115384615384616]
[6,28,2018,12,59,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T12:59:29",-0.22,-0.30230769230769228]
[6,28,2018,12,59,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:59:39",-0.20999999999999996,-0.30115384615384611]
[6,28,2018,12,59,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T12:59:49",-0.19499999999999998,-0.30346153846153845]
[6,28,2018,12,59,59,-0.12,-0.12,"2018-06-28T12:59:59",-0.18000000000000002,-0.30230769230769233]
[6,28,2018,13,0,9,-0.06,-0.06,"2018-06-28T13:00:09",-0.15000000000000002,-0.29076923076923084]
[6,28,2018,13,0,19,-0.06,-0.06,"2018-06-28T13:00:19",-0.125,-0.27461538461538465]
[6,28,2018,13,0,29,-0.06,-0.06,"2018-06-28T13:00:29",-0.10000000000000002,-0.25615384615384618]
[6,28,2018,13,0,39,-0.12,-0.12,"2018-06-28T13:00:39",-9.5000000000000015E-2,-0.24115384615384616]
[6,28,2018,13,0,49,-0.03,-0.03,"2018-06-28T13:00:49",-7.4999999999999997E-2,-0.2203846153846154]
[6,28,2018,13,0,59,-0.12,-0.12,"2018-06-28T13:00:59",-7.4999999999999997E-2,-0.20538461538461544]
[6,28,2018,13,1,9,-0.18,-0.18,"2018-06-28T13:01:09",-9.5000000000000015E-2,-0.20192307692307696]
[6,28,2018,13,1,19,-0.24,-0.24,"2018-06-28T13:01:19",-0.125,-0.19846153846153849]
[6,28,2018,13,1,29,-0.03,-0.03,"2018-06-28T13:01:29",-0.12,-0.18692307692307691]
[6,28,2018,13,1,39,-0.12,-0.12,{"$f":"DATE(C1657,A1657,B1657)+TIME(D1657,E1657,F1657)","v":"2018-06-28T13:01:39"},-0.12,-0.18000000000000002]
[6,28,2018,13,1,49,-0.09,-0.09,"2018-06-28T13:01:49",-0.13,-0.17192307692307696]
[6,28,2018,13,1,59,-0.06,-0.06,"2018-06-28T13:01:59",-0.12,-0.16269230769230764]
[6,28,2018,13,2,9,-0.03,-0.03,"2018-06-28T13:02:09",-9.5000000000000015E-2,-0.15346153846153845]
[6,28,2018,13,2,19,-0.03,-0.03,"2018-06-28T13:02:19",{"$f":"AVERAGE(G1656:G1661)","v":-0.06},-0.14423076923076922]
[6,28,2018,13,2,29,-0.03,-0.03,"2018-06-28T13:02:29",-6.0000000000000019E-2,-0.13384615384615381]
[6,28,2018,13,2,39,0,0,"2018-06-28T13:02:39",-0.04,-0.1246153846153846]
[6,28,2018,13,2,49,0,0,"2018-06-28T13:02:49",-2.4999999999999998E-2,-0.11538461538461536]
[6,28,2018,13,2,59,-0.09,-0.09,"2018-06-28T13:02:59",-0.03,-0.11076923076923074]
[6,28,2018,13,3,9,-0.12,-0.12,"2018-06-28T13:03:09",-4.5000000000000005E-2,-0.10615384615384613]
[6,28,2018,13,3,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:03:19",-6.5000000000000002E-2,-0.10384615384615382]
[6,28,2018,13,3,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:03:29",-8.5000000000000006E-2,-0.10038461538461535]
[6,28,2018,13,3,39,-0.18,-0.18,"2018-06-28T13:03:39",-0.11499999999999999,-9.9230769230769234E-2]
[6,28,2018,13,3,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:03:49",-0.15,-9.9230769230769234E-2]
[6,28,2018,13,3,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:03:59",-0.16,-9.9230769230769234E-2]
[6,28,2018,13,4,9,-0.24,-0.24,"2018-06-28T13:04:09",-0.18000000000000002,-0.10269230769230769]
[6,28,2018,13,4,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:04:19",-0.20499999999999999,-0.1096153846153846]
[6,28,2018,13,4,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:04:29",-0.23,-0.11884615384615384]
[6,28,2018,13,4,39,-0.27,-0.27,"2018-06-28T13:04:39",-0.24500000000000002,-0.12692307692307689]
[6,28,2018,13,4,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:04:49",-0.26000000000000006,-0.13615384615384615]
[6,28,2018,13,4,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:04:59",-0.27,-0.13961538461538461]
[6,28,2018,13,5,9,-0.24,-0.24,"2018-06-28T13:05:09",-0.27,-0.14769230769230768]
[6,28,2018,13,5,19,-0.18,-0.18,"2018-06-28T13:05:19",-0.25,-0.15]
[6,28,2018,13,5,29,-0.18,-0.18,"2018-06-28T13:05:29",-0.22999999999999998,-0.15000000000000005]
[6,28,2018,13,5,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:05:39",-0.21999999999999997,{"$f":"AVERAGE(G1656:G1681)","v":-0.14884615384615388}]
[6,28,2018,13,5,49,-0.24,-0.24,"2018-06-28T13:05:49",-0.21,-0.15692307692307697]
[6,28,2018,13,5,59,-0.27,-0.27,"2018-06-28T13:05:59",-0.22,-0.16269230769230772]
[6,28,2018,13,6,9,-0.24,-0.24,"2018-06-28T13:06:09",-0.22,-0.1684615384615385]
[6,28,2018,13,6,19,-0.24,-0.24,"2018-06-28T13:06:19",-0.23,-0.17538461538461542]
[6,28,2018,13,6,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:06:29",-0.23499999999999999,-0.18230769230769234]
[6,28,2018,13,6,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:06:39",-0.23499999999999999,-0.18923076923076929]
[6,28,2018,13,6,49,-0.24,-0.24,"2018-06-28T13:06:49",-0.23499999999999999,-0.19730769230769235]
[6,28,2018,13,6,59,-0.24,-0.24,"2018-06-28T13:06:59",-0.22999999999999998,-0.20653846153846159]
[6,28,2018,13,7,9,-0.24,-0.24,"2018-06-28T13:07:09",-0.23,-0.21576923076923082]
[6,28,2018,13,7,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:07:19",-0.215,-0.21807692307692314]
[6,28,2018,13,7,29,-0.12,-0.12,"2018-06-28T13:07:29",-0.20000000000000004,-0.21807692307692314]
[6,28,2018,13,7,39,-0.12,-0.12,"2018-06-28T13:07:39",-0.18499999999999997,-0.21692307692307697]
[6,28,2018,13,7,49,-0.18,-0.18,"2018-06-28T13:07:49",-0.17500000000000002,-0.21807692307692314]
[6,28,2018,13,7,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:07:59",-0.16,-0.21692307692307697]
[6,28,2018,13,8,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:08:09",-0.15500000000000003,-0.21692307692307697]
[6,28,2018,13,8,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:08:19",-0.18000000000000002,-0.22269230769230772]
[6,28,2018,13,8,29,-0.33,-0.33,"2018-06-28T13:08:29",-0.215,-0.22615384615384618]
[6,28,2018,13,8,39,-0.27,-0.27,"2018-06-28T13:08:39",-0.24000000000000002,-0.22500000000000006]
[6,28,2018,13,8,49,-0.24,-0.24,"2018-06-28T13:08:49",-0.25000000000000006,-0.22269230769230772]
[6,28,2018,13,8,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:08:59",-0.26,-0.22038461538461543]
[6,28,2018,13,9,9,-0.18,-0.18,"2018-06-28T13:09:09",-0.255,-0.21576923076923077]
[6,28,2018,13,9,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:09:19",-0.24,-0.21576923076923082]
[6,28,2018,13,9,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:09:29",-0.21999999999999997,-0.21461538461538465]
[6,28,2018,13,9,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:09:39",-0.21,-0.21576923076923082]
[6,28,2018,13,9,49,-0.24,-0.24,"2018-06-28T13:09:49",-0.21,-0.21807692307692308]
[6,28,2018,13,9,59,-0.18,-0.18,"2018-06-28T13:09:59",-0.20499999999999999,-0.21692307692307691]
[6,28,2018,13,10,9,-0.18,-0.18,"2018-06-28T13:10:09",-0.20499999999999999,-0.2146153846153846]
[6,28,2018,13,10,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:10:19",-0.20499999999999999,-0.21230769230769228]
[6,28,2018,13,10,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:10:29",-0.20499999999999999,-0.21115384615384616]
[6,28,2018,13,10,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:10:39",-0.19499999999999998,-0.2076923076923077]
[6,28,2018,13,10,49,-0.24,-0.24,"2018-06-28T13:10:49",-0.19499999999999998,-0.20884615384615388]
[6,28,2018,13,10,59,-0.24,-0.24,"2018-06-28T13:10:59",-0.20499999999999999,-0.21]
[6,28,2018,13,11,9,-0.27,-0.27,"2018-06-28T13:11:09",-0.22,-0.21115384615384616]
[6,28,2018,13,11,19,-0.27,-0.27,"2018-06-28T13:11:19",-0.23,-0.21230769230769236]
[6,28,2018,13,11,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:11:29",-0.22999999999999998,-0.21115384615384619]
[6,28,2018,13,11,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:11:39",-0.24,-0.21346153846153848]
[6,28,2018,13,11,49,-0.18,-0.18,"2018-06-28T13:11:49",-0.22999999999999998,-0.21576923076923074]
[6,28,2018,13,11,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:11:59",-0.22499999999999998,-0.21923076923076923]
[6,28,2018,13,12,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:12:09",-0.215,-0.22038461538461535]
[6,28,2018,13,12,19,-0.21000000000000002,-0.21000000000000002,{"$f":"DATE(C1721,A1721,B1721)+TIME(D1721,E1721,F1721)","v":"2018-06-28T13:12:19"},-0.20499999999999999,-0.22269230769230769]
[6,28,2018,13,12,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:12:29",-0.20499999999999999,-0.22269230769230766]
[6,28,2018,13,12,39,-0.24,-0.24,"2018-06-28T13:12:39",-0.21,-0.22038461538461537]
[6,28,2018,13,12,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:12:49",-0.20499999999999999,-0.21346153846153845]
[6,28,2018,13,12,59,-0.12,-0.12,"2018-06-28T13:12:59",{"$f":"AVERAGE(G1720:G1725)","v":-0.19000000000000003},-0.2076923076923077]
[6,28,2018,13,13,9,-0.12,-0.12,"2018-06-28T13:13:09",-0.17500000000000002,-0.20307692307692313]
[6,28,2018,13,13,19,-0.12,-0.12,"2018-06-28T13:13:19",-0.16,-0.19961538461538467]
[6,28,2018,13,13,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:13:29",-0.15,-0.19846153846153852]
[6,28,2018,13,13,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:13:39",-0.13500000000000001,-0.19615384615384621]
[6,28,2018,13,13,49,-0.06,-0.06,"2018-06-28T13:13:49",-0.12,-0.19038461538461543]
[6,28,2018,13,13,59,-0.06,-0.06,"2018-06-28T13:13:59",-0.11000000000000003,-0.18461538461538465]
[6,28,2018,13,14,9,-0.18,-0.18,"2018-06-28T13:14:09",-0.12,-0.18230769230769228]
[6,28,2018,13,14,19,-0.18,-0.18,"2018-06-28T13:14:19",-0.13,-0.18230769230769228]
[6,28,2018,13,14,29,-0.09,-0.09,"2018-06-28T13:14:29",-0.12,-0.17884615384615382]
[6,28,2018,13,14,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:14:39",-0.12,-0.17653846153846153]
[6,28,2018,13,14,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:14:49",-0.16,-0.18]
[6,28,2018,13,14,59,-0.39,-0.39,"2018-06-28T13:14:59",-0.215,-0.18923076923076926]
[6,28,2018,13,15,9,-0.24,-0.24,"2018-06-28T13:15:09",-0.22500000000000001,-0.18923076923076923]
[6,28,2018,13,15,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:15:19",-0.245,-0.19153846153846152]
[6,28,2018,13,15,29,-0.24,-0.24,"2018-06-28T13:15:29",-0.27,-0.1903846153846154]
[6,28,2018,13,15,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:15:39",-0.27,-0.1857692307692308]
[6,28,2018,13,15,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:15:49",-0.25499999999999995,-0.1857692307692308]
[6,28,2018,13,15,59,-0.24,-0.24,"2018-06-28T13:15:59",-0.23,-0.18692307692307697]
[6,28,2018,13,16,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:16:09",-0.22500000000000001,-0.18807692307692309]
[6,28,2018,13,16,19,-0.18,-0.18,"2018-06-28T13:16:19",-0.20499999999999999,{"$f":"AVERAGE(G1720:G1745)","v":-0.18692307692307694}]
[6,28,2018,13,16,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:16:29",-0.19999999999999998,-0.18692307692307691]
[6,28,2018,13,16,39,-0.24,-0.24,"2018-06-28T13:16:39",-0.215,-0.18807692307692306]
[6,28,2018,13,16,49,-0.24,-0.24,"2018-06-28T13:16:49",-0.22,-0.18923076923076923]
[6,28,2018,13,16,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:16:59",-0.20499999999999999,-0.1857692307692308]
[6,28,2018,13,17,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:17:09",-0.20499999999999999,-0.18807692307692309]
[6,28,2018,13,17,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:17:19",-0.21,-0.19153846153846155]
[6,28,2018,13,17,29,-0.27,-0.27,"2018-06-28T13:17:29",-0.22,-0.19730769230769235]
[6,28,2018,13,17,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:17:39",-0.215,-0.20076923076923076]
[6,28,2018,13,17,49,-0.27,-0.27,"2018-06-28T13:17:49",-0.22,-0.20538461538461539]
[6,28,2018,13,17,59,-0.27,-0.27,"2018-06-28T13:17:59",-0.24000000000000002,-0.21000000000000002]
[6,28,2018,13,18,9,-0.24,-0.24,"2018-06-28T13:18:09",-0.245,-0.21692307692307694]
[6,28,2018,13,18,19,-0.27,-0.27,"2018-06-28T13:18:19",-0.255,-0.22499999999999998]
[6,28,2018,13,18,29,-0.27,-0.27,"2018-06-28T13:18:29",-0.255,-0.22846153846153844]
[6,28,2018,13,18,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:18:39",-0.27,-0.23307692307692299]
[6,28,2018,13,18,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:18:49",-0.25,-0.23538461538461533]
[6,28,2018,13,18,59,-0.24,-0.24,"2018-06-28T13:18:59",-0.245,-0.23884615384615385]
[6,28,2018,13,19,9,-0.12,-0.12,"2018-06-28T13:19:09",-0.22500000000000001,-0.2319230769230769]
[6,28,2018,13,19,19,-0.03,-0.03,"2018-06-28T13:19:19",-0.18500000000000003,-0.21807692307692311]
[6,28,2018,13,19,29,-0.03,-0.03,"2018-06-28T13:19:29",-0.14500000000000002,-0.21000000000000002]
[6,28,2018,13,19,39,-0.03,-0.03,"2018-06-28T13:19:39",-0.10000000000000002,-0.19961538461538464]
[6,28,2018,13,19,49,-0.03,-0.03,"2018-06-28T13:19:49",-8.0000000000000016E-2,-0.1915384615384616]
[6,28,2018,13,19,59,-0.03,-0.03,"2018-06-28T13:19:59",-4.5000000000000005E-2,-0.186923076923077]
[6,28,2018,13,20,9,0,0,"2018-06-28T13:20:09",-2.4999999999999998E-2,-0.17884615384615393]
[6,28,2018,13,20,19,-0.03,-0.03,"2018-06-28T13:20:19",-2.4999999999999998E-2,-0.17076923076923081]
[6,28,2018,13,20,29,-0.09,-0.09,"2018-06-28T13:20:29",-3.4999999999999996E-2,-0.16615384615384621]
[6,28,2018,13,20,39,-0.09,-0.09,"2018-06-28T13:20:39",-4.5000000000000005E-2,-0.16269230769230764]
[6,28,2018,13,20,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:20:49",-6.5000000000000002E-2,-0.16038461538461535]
[6,28,2018,13,20,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:20:59",-9.5000000000000015E-2,-0.15923076923076918]
[6,28,2018,13,21,9,-0.27,-0.27,"2018-06-28T13:21:09",-0.14000000000000001,-0.16038461538461532]
[6,28,2018,13,21,19,-0.39,-0.39,"2018-06-28T13:21:19",-0.20000000000000004,-0.16961538461538456]
[6,28,2018,13,21,29,-0.42000000000000004,-0.42000000000000004,"2018-06-28T13:21:29",-0.25500000000000006,-0.17769230769230759]
[6,28,2018,13,21,39,-0.44999999999999996,-0.44999999999999996,"2018-06-28T13:21:39",-0.315,-0.18692307692307691]
[6,28,2018,13,21,49,-0.48,-0.48,"2018-06-28T13:21:49",-0.36999999999999994,-0.19499999999999995]
[6,28,2018,13,21,59,-0.48,-0.48,"2018-06-28T13:21:59",-0.41499999999999998,-0.2053846153846153]
[6,28,2018,13,22,9,-0.36,-0.36,"2018-06-28T13:22:09",-0.42999999999999994,-0.20884615384615388]
[6,28,2018,13,22,19,-0.33,-0.33,"2018-06-28T13:22:19",-0.42,-0.21115384615384619]
[6,28,2018,13,22,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:22:29",-0.40000000000000008,-0.21346153846153848]
[6,28,2018,13,22,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:22:39",-0.375,-0.21461538461538462]
[6,28,2018,13,22,49,-0.33,-0.33,"2018-06-28T13:22:49",-0.35000000000000003,-0.21692307692307694]
[6,28,2018,13,22,59,-0.39,-0.39,{"$f":"DATE(C1785,A1785,B1785)+TIME(D1785,E1785,F1785)","v":"2018-06-28T13:22:59"},-0.33500000000000002,-0.22038461538461537]
[6,28,2018,13,23,9,-0.36,-0.36,"2018-06-28T13:23:09",-0.33500000000000002,-0.22846153846153844]
[6,28,2018,13,23,19,-0.39,-0.39,"2018-06-28T13:23:19",-0.34500000000000003,-0.23423076923076919]
[6,28,2018,13,23,29,-0.33,-0.33,"2018-06-28T13:23:29",-0.35000000000000003,-0.24230769230769231]
[6,28,2018,13,23,39,-0.36,-0.36,"2018-06-28T13:23:39",{"$f":"AVERAGE(G1784:G1789)","v":-0.36000000000000004},-0.255]
[6,28,2018,13,23,49,-0.33,-0.33,"2018-06-28T13:23:49",-0.36000000000000004,-0.26653846153846156]
[6,28,2018,13,23,59,-0.36,-0.36,"2018-06-28T13:23:59",-0.35499999999999998,-0.27923076923076928]
[6,28,2018,13,24,9,-0.39,-0.39,"2018-06-28T13:24:09",-0.36000000000000004,-0.29307692307692307]
[6,28,2018,13,24,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:24:19",-0.34500000000000003,-0.30346153846153845]
[6,28,2018,13,24,29,-0.39,-0.39,"2018-06-28T13:24:29",-0.35499999999999998,-0.31846153846153846]
[6,28,2018,13,24,39,-0.39,-0.39,"2018-06-28T13:24:39",-0.36000000000000004,-0.3323076923076923]
[6,28,2018,13,24,49,-0.51,-0.51,"2018-06-28T13:24:49",-0.38999999999999996,-0.34846153846153849]
[6,28,2018,13,24,59,-0.36,-0.36,"2018-06-28T13:24:59",-0.39000000000000007,-0.35884615384615387]
[6,28,2018,13,25,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T13:25:09",-0.40000000000000008,-0.37038461538461526]
[6,28,2018,13,25,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T13:25:19",-0.41999999999999993,-0.3784615384615384]
[6,28,2018,13,25,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:25:29",-0.40499999999999997,-0.37961538461538458]
[6,28,2018,13,25,39,-0.27,-0.27,"2018-06-28T13:25:39",-0.38500000000000001,-0.37499999999999994]
[6,28,2018,13,25,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:25:49",-0.33500000000000002,-0.36692307692307696]
[6,28,2018,13,25,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:25:59",-0.31,-0.35769230769230781]
[6,28,2018,13,26,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:26:09",-0.27,-0.34730769230769237]
[6,28,2018,13,26,19,-0.24,-0.24,"2018-06-28T13:26:19",-0.24,-0.33807692307692316]
[6,28,2018,13,26,29,-0.27,-0.27,"2018-06-28T13:26:29",-0.23500000000000001,-0.33461538461538459]
[6,28,2018,13,26,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:26:39",-0.22500000000000001,-0.33]
[6,28,2018,13,26,49,-0.18,-0.18,"2018-06-28T13:26:49",-0.22,-0.32538461538461544]
[6,28,2018,13,26,59,-0.12,-0.12,"2018-06-28T13:26:59",-0.20499999999999999,{"$f":"AVERAGE(G1784:G1809)","v":-0.31846153846153852}]
[6,28,2018,13,27,9,-0.12,-0.12,"2018-06-28T13:27:09",-0.19000000000000003,-0.31038461538461537]
[6,28,2018,13,27,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:27:19",-0.17500000000000002,-0.30115384615384622]
[6,28,2018,13,27,29,-0.18,-0.18,"2018-06-28T13:27:29",-0.16,-0.2942307692307693]
[6,28,2018,13,27,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:27:39",-0.16,-0.28730769230769232]
[6,28,2018,13,27,49,-0.24,-0.24,"2018-06-28T13:27:49",-0.17,-0.28384615384615386]
[6,28,2018,13,27,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:27:59",-0.18500000000000003,-0.27807692307692305]
[6,28,2018,13,28,9,-0.24,-0.24,"2018-06-28T13:28:09",-0.20499999999999999,-0.27461538461538459]
[6,28,2018,13,28,19,-0.24,-0.24,"2018-06-28T13:28:19",-0.22,-0.27]
[6,28,2018,13,28,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:28:29",-0.22500000000000001,-0.26307692307692315]
[6,28,2018,13,28,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:28:39",-0.22499999999999998,-0.25961538461538458]
[6,28,2018,13,28,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:28:49",-0.20999999999999996,-0.25038461538461543]
[6,28,2018,13,28,59,-0.12,-0.12,"2018-06-28T13:28:59",-0.19499999999999998,-0.24000000000000005]
[6,28,2018,13,29,9,-0.06,-0.06,"2018-06-28T13:29:09",-0.16500000000000001,-0.22269230769230772]
[6,28,2018,13,29,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:29:19",-0.15,-0.21461538461538465]
[6,28,2018,13,29,29,-0.12,-0.12,"2018-06-28T13:29:29",-0.13500000000000001,-0.20192307692307696]
[6,28,2018,13,29,39,-0.18,-0.18,"2018-06-28T13:29:39",-0.13,-0.19269230769230772]
[6,28,2018,13,29,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:29:49",-0.14000000000000001,-0.18923076923076926]
[6,28,2018,13,29,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:29:59",-0.14499999999999999,-0.18461538461538465]
[6,28,2018,13,30,9,-0.12,-0.12,"2018-06-28T13:30:09",-0.155,-0.18115384615384617]
[6,28,2018,13,30,19,-0.03,-0.03,"2018-06-28T13:30:19",-0.13500000000000001,-0.17423076923076927]
[6,28,2018,13,30,29,-0.09,-0.09,"2018-06-28T13:30:29",-0.13,-0.16961538461538467]
[6,28,2018,13,30,39,-0.03,-0.03,"2018-06-28T13:30:39",-0.105,-0.16153846153846155]
[6,28,2018,13,30,49,-0.09,-0.09,"2018-06-28T13:30:49",-8.5000000000000006E-2,-0.1546153846153846]
[6,28,2018,13,30,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:30:59",-8.5000000000000006E-2,-0.15230769230769228]
[6,28,2018,13,31,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:31:09",-0.10000000000000002,-0.15346153846153843]
[6,28,2018,13,31,19,-0.18,-0.18,"2018-06-28T13:31:19",-0.125,-0.15576923076923077]
[6,28,2018,13,31,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:31:29",-0.14500000000000002,-0.15923076923076923]
[6,28,2018,13,31,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:31:39",-0.19000000000000003,-0.16500000000000001]
[6,28,2018,13,31,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:31:49",-0.20000000000000004,-0.16384615384615384]
[6,28,2018,13,31,59,-0.12,-0.12,"2018-06-28T13:31:59",-0.19500000000000006,-0.16038461538461538]
[6,28,2018,13,32,9,-0.09,-0.09,"2018-06-28T13:32:09",-0.17500000000000002,-0.1546153846153846]
[6,28,2018,13,32,19,-0.18,-0.18,"2018-06-28T13:32:19",-0.17500000000000002,-0.15346153846153843]
[6,28,2018,13,32,29,-0.18,-0.18,"2018-06-28T13:32:29",-0.17,-0.15115384615384617]
[6,28,2018,13,32,39,-0.09,-0.09,"2018-06-28T13:32:39",-0.13499999999999998,-0.14538461538461542]
[6,28,2018,13,32,49,-0.24,-0.24,"2018-06-28T13:32:49",-0.15,-0.14653846153846156]
[6,28,2018,13,32,59,-0.24,-0.24,"2018-06-28T13:32:59",-0.17,-0.14769230769230773]
[6,28,2018,13,33,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:33:09",-0.20499999999999999,-0.15346153846153848]
[6,28,2018,13,33,19,-0.24,-0.24,"2018-06-28T13:33:19",-0.215,-0.15807692307692309]
[6,28,2018,13,33,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:33:29",-0.21999999999999997,-0.16384615384615386]
[6,28,2018,13,33,39,-0.24,-0.24,{"$f":"DATE(C1849,A1849,B1849)+TIME(D1849,E1849,F1849)","v":"2018-06-28T13:33:39"},-0.245,-0.16730769230769232]
[6,28,2018,13,33,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T13:33:49",-0.24,-0.17076923076923078]
[6,28,2018,13,33,59,-0.24,-0.24,"2018-06-28T13:33:59",-0.24,-0.1730769230769231]
[6,28,2018,13,34,9,-0.24,-0.24,"2018-06-28T13:34:09",-0.22999999999999998,-0.17423076923076927]
[6,28,2018,13,34,19,-0.27,-0.27,"2018-06-28T13:34:19",{"$f":"AVERAGE(G1848:G1853)","v":-0.23500000000000001},-0.17884615384615385]
[6,28,2018,13,34,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:34:29",-0.25,-0.1857692307692308]
[6,28,2018,13,34,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:34:39",-0.26,-0.19615384615384621]
[6,28,2018,13,34,49,-0.42000000000000004,-0.42000000000000004,"2018-06-28T13:34:49",-0.29499999999999998,-0.2088461538461539]
[6,28,2018,13,34,59,-0.36,-0.36,"2018-06-28T13:34:59",-0.315,-0.22153846153846157]
[6,28,2018,13,35,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T13:35:09",-0.34499999999999997,-0.23423076923076927]
[6,28,2018,13,35,19,-0.48,-0.48,"2018-06-28T13:35:19",-0.37999999999999995,-0.24692307692307691]
[6,28,2018,13,35,29,-0.54,-0.54,"2018-06-28T13:35:29",-0.42,-0.25961538461538464]
[6,28,2018,13,35,39,-0.63,-0.63,"2018-06-28T13:35:39",-0.47500000000000003,-0.27692307692307694]
[6,28,2018,13,35,49,-0.57000000000000006,-0.57000000000000006,"2018-06-28T13:35:49",-0.5,-0.29076923076923078]
[6,28,2018,13,35,59,-0.54,-0.54,"2018-06-28T13:35:59",-0.52999999999999992,-0.30000000000000004]
[6,28,2018,13,36,9,-0.57000000000000006,-0.57000000000000006,"2018-06-28T13:36:09",-0.55500000000000005,-0.31615384615384617]
[6,28,2018,13,36,19,-0.60000000000000009,-0.60000000000000009,"2018-06-28T13:36:19",-0.57500000000000007,-0.33461538461538459]
[6,28,2018,13,36,29,-0.48,-0.48,"2018-06-28T13:36:29",-0.56500000000000006,-0.34961538461538461]
[6,28,2018,13,36,39,-0.51,-0.51,"2018-06-28T13:36:39",-0.54500000000000004,-0.36230769230769239]
[6,28,2018,13,36,49,-0.48,-0.48,"2018-06-28T13:36:49",-0.53,-0.37384615384615394]
[6,28,2018,13,36,59,-0.36,-0.36,"2018-06-28T13:36:59",-0.5,-0.38423076923076932]
[6,28,2018,13,37,9,-0.39,-0.39,"2018-06-28T13:37:09",-0.47000000000000003,-0.39]
[6,28,2018,13,37,19,-0.39,-0.39,"2018-06-28T13:37:19",-0.43500000000000005,-0.39576923076923082]
[6,28,2018,13,37,29,-0.36,-0.36,"2018-06-28T13:37:29",-0.41500000000000004,-0.39807692307692311]
[6,28,2018,13,37,39,-0.44999999999999996,-0.44999999999999996,"2018-06-28T13:37:39",-0.40499999999999997,{"$f":"AVERAGE(G1848:G1873)","v":-0.4061538461538462}]
[6,28,2018,13,37,49,-0.63,-0.63,"2018-06-28T13:37:49",-0.43,-0.42230769230769233]
[6,28,2018,13,37,59,-0.57000000000000006,-0.57000000000000006,"2018-06-28T13:37:59",-0.46500000000000002,-0.43500000000000011]
[6,28,2018,13,38,9,-0.57000000000000006,-0.57000000000000006,"2018-06-28T13:38:09",-0.49500000000000011,-0.44884615384615389]
[6,28,2018,13,38,19,-0.63,-0.63,"2018-06-28T13:38:19",-0.53500000000000003,-0.46384615384615391]
[6,28,2018,13,38,29,-0.48,-0.48,"2018-06-28T13:38:29",-0.55500000000000005,-0.47307692307692317]
[6,28,2018,13,38,39,-0.33,-0.33,"2018-06-28T13:38:39",-0.53500000000000003,-0.47538461538461552]
[6,28,2018,13,38,49,-0.27,-0.27,"2018-06-28T13:38:49",-0.47500000000000003,-0.47423076923076929]
[6,28,2018,13,38,59,-0.33,-0.33,"2018-06-28T13:38:59",-0.43500000000000005,-0.47538461538461552]
[6,28,2018,13,39,9,-0.36,-0.36,"2018-06-28T13:39:09",-0.39999999999999997,-0.47307692307692317]
[6,28,2018,13,39,19,-0.51,-0.51,"2018-06-28T13:39:19",-0.38000000000000006,-0.47884615384615387]
[6,28,2018,13,39,29,-0.60000000000000009,-0.60000000000000009,"2018-06-28T13:39:29",-0.40000000000000008,-0.48576923076923079]
[6,28,2018,13,39,39,-0.66,-0.66,"2018-06-28T13:39:39",-0.45500000000000007,-0.49269230769230771]
[6,28,2018,13,39,49,-0.72,-0.72,"2018-06-28T13:39:49",-0.52999999999999992,-0.49961538461538468]
[6,28,2018,13,39,59,-0.86999999999999988,-0.86999999999999988,"2018-06-28T13:39:59",-0.62000000000000011,-0.50884615384615384]
[6,28,2018,13,40,9,-0.66,-0.66,"2018-06-28T13:40:09",-0.67,-0.51230769230769235]
[6,28,2018,13,40,19,-0.66,-0.66,"2018-06-28T13:40:19",-0.69499999999999995,-0.51692307692307693]
[6,28,2018,13,40,29,-0.63,-0.63,"2018-06-28T13:40:29",-0.70000000000000007,-0.51923076923076927]
[6,28,2018,13,40,39,-0.54,-0.54,"2018-06-28T13:40:39",-0.68,-0.51692307692307693]
[6,28,2018,13,40,49,-0.42000000000000004,-0.42000000000000004,"2018-06-28T13:40:49",-0.63,-0.5146153846153847]
[6,28,2018,13,40,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T13:40:59",-0.55500000000000005,-0.51115384615384629]
[6,28,2018,13,41,9,-0.54,-0.54,"2018-06-28T13:41:09",-0.53500000000000003,-0.51346153846153852]
[6,28,2018,13,41,19,-0.51,-0.51,"2018-06-28T13:41:19",-0.5099999999999999,-0.51923076923076927]
[6,28,2018,13,41,29,-0.54,-0.54,"2018-06-28T13:41:29",-0.49500000000000005,-0.52500000000000013]
[6,28,2018,13,41,39,-0.44999999999999996,-0.44999999999999996,"2018-06-28T13:41:39",-0.48,-0.52730769230769237]
[6,28,2018,13,41,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T13:41:49",-0.48500000000000004,-0.53076923076923077]
[6,28,2018,13,41,59,-0.36,-0.36,"2018-06-28T13:41:59",-0.47500000000000003,-0.52730769230769237]
[6,28,2018,13,42,9,-0.36,-0.36,"2018-06-28T13:42:09",-0.44500000000000001,-0.51692307692307682]
[6,28,2018,13,42,19,-0.39,-0.39,"2018-06-28T13:42:19",-0.42499999999999999,-0.5099999999999999]
[6,28,2018,13,42,29,-0.48,-0.48,"2018-06-28T13:42:29",-0.41499999999999998,-0.50653846153846149]
[6,28,2018,13,42,39,-0.54,-0.54,"2018-06-28T13:42:39",-0.43,-0.50307692307692298]
[6,28,2018,13,42,49,-0.63,-0.63,"2018-06-28T13:42:49",-0.45999999999999996,-0.50884615384615384]
[6,28,2018,13,42,59,-0.60000000000000009,-0.60000000000000009,"2018-06-28T13:42:59",-0.5,-0.51923076923076927]
[6,28,2018,13,43,9,-0.57000000000000006,-0.57000000000000006,"2018-06-28T13:43:09",-0.53500000000000003,-0.53076923076923066]
[6,28,2018,13,43,19,-0.63,-0.63,"2018-06-28T13:43:19",-0.57500000000000007,-0.54230769230769227]
[6,28,2018,13,43,29,-0.60000000000000009,-0.60000000000000009,"2018-06-28T13:43:29",-0.59499999999999997,-0.55153846153846153]
[6,28,2018,13,43,39,-0.66,-0.66,"2018-06-28T13:43:39",-0.6150000000000001,-0.55730769230769228]
[6,28,2018,13,43,49,-0.54,-0.54,"2018-06-28T13:43:49",-0.60000000000000009,-0.55499999999999994]
[6,28,2018,13,43,59,-0.54,-0.54,"2018-06-28T13:43:59",-0.59000000000000008,-0.55038461538461547]
[6,28,2018,13,44,9,-0.48,-0.48,"2018-06-28T13:44:09",-0.57500000000000007,-0.54115384615384621]
[6,28,2018,13,44,19,-0.48,-0.48,{"$f":"DATE(C1913,A1913,B1913)+TIME(D1913,E1913,F1913)","v":"2018-06-28T13:44:19"},-0.55000000000000004,-0.52615384615384619]
[6,28,2018,13,44,29,-0.48,-0.48,"2018-06-28T13:44:29",-0.53,-0.51923076923076927]
[6,28,2018,13,44,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T13:44:39",-0.49,-0.51]
[6,28,2018,13,44,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T13:44:49",-0.47499999999999992,-0.50307692307692309]
[6,28,2018,13,44,59,-0.44999999999999996,-0.44999999999999996,"2018-06-28T13:44:59",{"$f":"AVERAGE(G1912:G1917)","v":-0.45999999999999996},-0.49961538461538463]
[6,28,2018,13,45,9,-0.51,-0.51,"2018-06-28T13:45:09",-0.46500000000000002,-0.50307692307692298]
[6,28,2018,13,45,19,-0.51,-0.51,"2018-06-28T13:45:19",-0.47000000000000003,-0.50653846153846149]
[6,28,2018,13,45,29,-0.66,-0.66,"2018-06-28T13:45:29",-0.5,-0.51115384615384618]
[6,28,2018,13,45,39,-0.81,-0.81,"2018-06-28T13:45:39",-0.56500000000000006,-0.52269230769230779]
[6,28,2018,13,45,49,-0.81,-0.81,"2018-06-28T13:45:49",-0.625,-0.53307692307692311]
[6,28,2018,13,45,59,-0.63,-0.63,"2018-06-28T13:45:59",-0.65500000000000003,-0.54]
[6,28,2018,13,46,9,-0.66,-0.66,"2018-06-28T13:46:09",-0.68,-0.54807692307692313]
[6,28,2018,13,46,19,-0.66,-0.66,"2018-06-28T13:46:19",-0.70500000000000007,-0.55961538461538474]
[6,28,2018,13,46,29,-0.66,-0.66,"2018-06-28T13:46:29",-0.70500000000000007,-0.57115384615384623]
[6,28,2018,13,46,39,-0.60000000000000009,-0.60000000000000009,"2018-06-28T13:46:39",-0.67,-0.57923076923076933]
[6,28,2018,13,46,49,-0.51,-0.51,"2018-06-28T13:46:49",-0.62000000000000011,-0.5803846153846155]
[6,28,2018,13,46,59,-0.39,-0.39,"2018-06-28T13:46:59",-0.57999999999999996,-0.57461538461538475]
[6,28,2018,13,47,9,-0.48,-0.48,"2018-06-28T13:47:09",-0.55000000000000004,-0.568846153846154]
[6,28,2018,13,47,19,-0.48,-0.48,"2018-06-28T13:47:19",-0.52,-0.56423076923076931]
[6,28,2018,13,47,29,-0.48,-0.48,"2018-06-28T13:47:29",-0.49,-0.56076923076923091]
[6,28,2018,13,47,39,-0.48,-0.48,"2018-06-28T13:47:39",-0.47,-0.55500000000000016]
[6,28,2018,13,47,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T13:47:49",-0.45999999999999996,-0.5492307692307693]
[6,28,2018,13,47,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T13:47:59",-0.46500000000000002,-0.54]
[6,28,2018,13,48,9,-0.54,-0.54,"2018-06-28T13:48:09",-0.47500000000000003,-0.53999999999999992]
[6,28,2018,13,48,19,-0.54,-0.54,"2018-06-28T13:48:19",-0.48500000000000004,{"$f":"AVERAGE(G1912:G1937)","v":-0.53999999999999992}]
[6,28,2018,13,48,29,-0.54,-0.54,"2018-06-28T13:48:29",-0.49500000000000005,-0.54230769230769227]
[6,28,2018,13,48,39,-0.51,-0.51,"2018-06-28T13:48:39",-0.5,-0.54346153846153844]
[6,28,2018,13,48,49,-0.51,-0.51,"2018-06-28T13:48:49",-0.5099999999999999,-0.54461538461538461]
[6,28,2018,13,48,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:48:59",-0.48999999999999994,-0.53999999999999992]
[6,28,2018,13,49,9,-0.27,-0.27,"2018-06-28T13:49:09",-0.44500000000000006,-0.533076923076923]
[6,28,2018,13,49,19,-0.27,-0.27,"2018-06-28T13:49:19",-0.39999999999999997,-0.52615384615384597]
[6,28,2018,13,49,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:49:29",-0.33500000000000002,-0.51230769230769224]
[6,28,2018,13,49,39,0,0,"2018-06-28T13:49:39",-0.25,-0.4926923076923076]
[6,28,2018,13,49,49,-0.18,-0.18,"2018-06-28T13:49:49",-0.19500000000000003,-0.47423076923076912]
[6,28,2018,13,49,59,-0.39,-0.39,"2018-06-28T13:49:59",-0.21000000000000005,-0.45807692307692316]
[6,28,2018,13,50,9,-0.48,-0.48,"2018-06-28T13:50:09",-0.24500000000000002,-0.44538461538461543]
[6,28,2018,13,50,19,-0.54,-0.54,"2018-06-28T13:50:19",-0.28999999999999998,-0.44192307692307697]
[6,28,2018,13,50,29,-0.57000000000000006,-0.57000000000000006,"2018-06-28T13:50:29",-0.36000000000000004,-0.43846153846153857]
[6,28,2018,13,50,39,-0.60000000000000009,-0.60000000000000009,"2018-06-28T13:50:39",-0.46,-0.43615384615384623]
[6,28,2018,13,50,49,-0.66,-0.66,"2018-06-28T13:50:49",-0.54,-0.43615384615384623]
[6,28,2018,13,50,59,-0.63,-0.63,"2018-06-28T13:50:59",-0.58000000000000007,-0.43730769230769223]
[6,28,2018,13,51,9,-0.66,-0.66,"2018-06-28T13:51:09",-0.61,-0.44307692307692303]
[6,28,2018,13,51,19,-0.63,-0.63,"2018-06-28T13:51:19",-0.625,-0.4523076923076923]
[6,28,2018,13,51,29,-0.54,-0.54,"2018-06-28T13:51:29",-0.62,-0.45461538461538464]
[6,28,2018,13,51,39,-0.51,-0.51,"2018-06-28T13:51:39",-0.60499999999999998,-0.45576923076923076]
[6,28,2018,13,51,49,-0.42000000000000004,-0.42000000000000004,"2018-06-28T13:51:49",-0.56499999999999995,-0.45346153846153858]
[6,28,2018,13,51,59,-0.48,-0.48,"2018-06-28T13:51:59",-0.53999999999999992,-0.45346153846153858]
[6,28,2018,13,52,9,-0.57000000000000006,-0.57000000000000006,"2018-06-28T13:52:09",-0.52500000000000002,-0.45807692307692321]
[6,28,2018,13,52,19,-0.69000000000000006,-0.69000000000000006,"2018-06-28T13:52:19",-0.53500000000000003,-0.46846153846153854]
[6,28,2018,13,52,29,-0.81,-0.81,"2018-06-28T13:52:29",-0.58000000000000007,-0.47884615384615398]
[6,28,2018,13,52,39,-0.81,-0.81,"2018-06-28T13:52:39",-0.63,-0.48923076923076925]
[6,28,2018,13,52,49,-0.81,-0.81,"2018-06-28T13:52:49",-0.69499999999999995,-0.49961538461538474]
[6,28,2018,13,52,59,-0.86999999999999988,-0.86999999999999988,"2018-06-28T13:52:59",-0.76000000000000012,-0.51346153846153852]
[6,28,2018,13,53,9,-0.92999999999999994,-0.92999999999999994,"2018-06-28T13:53:09",-0.82,-0.5296153846153846]
[6,28,2018,13,53,19,-0.89999999999999991,-0.89999999999999991,"2018-06-28T13:53:19",-0.85499999999999987,-0.5526923076923077]
[6,28,2018,13,53,29,-0.81,-0.81,"2018-06-28T13:53:29",-0.85500000000000009,-0.57346153846153858]
[6,28,2018,13,53,39,-0.54,-0.54,"2018-06-28T13:53:39",-0.81,-0.58384615384615379]
[6,28,2018,13,53,49,-0.60000000000000009,-0.60000000000000009,"2018-06-28T13:53:49",-0.77500000000000002,-0.60115384615384615]
[6,28,2018,13,53,59,-0.66,-0.66,"2018-06-28T13:53:59",-0.73999999999999988,-0.62653846153846149]
[6,28,2018,13,54,9,-0.86999999999999988,-0.86999999999999988,"2018-06-28T13:54:09",-0.73,-0.65307692307692311]
[6,28,2018,13,54,19,-1.08,-1.08,"2018-06-28T13:54:19",-0.76000000000000012,-0.67961538461538473]
[6,28,2018,13,54,29,-1.1099999999999999,-1.1099999999999999,"2018-06-28T13:54:29",-0.80999999999999994,-0.70384615384615379]
[6,28,2018,13,54,39,-0.66,-0.66,"2018-06-28T13:54:39",-0.83000000000000007,-0.70846153846153836]
[6,28,2018,13,54,49,-0.69000000000000006,-0.69000000000000006,"2018-06-28T13:54:49",-0.84500000000000008,-0.71307692307692305]
[6,28,2018,13,54,59,-0.54,-0.54,{"$f":"DATE(C1977,A1977,B1977)+TIME(D1977,E1977,F1977)","v":"2018-06-28T13:54:59"},-0.82500000000000007,-0.71076923076923082]
[6,28,2018,13,55,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T13:55:09",-0.75,-0.70153846153846144]
[6,28,2018,13,55,19,-0.60000000000000009,-0.60000000000000009,"2018-06-28T13:55:19",-0.66999999999999993,-0.70038461538461561]
[6,28,2018,13,55,29,-0.54,-0.54,"2018-06-28T13:55:29",-0.57500000000000007,-0.69576923076923092]
[6,28,2018,13,55,39,-0.54,-0.54,"2018-06-28T13:55:39",{"$f":"AVERAGE(G1976:G1981)","v":-0.55500000000000005},-0.69230769230769229]
[6,28,2018,13,55,49,-0.51,-0.51,"2018-06-28T13:55:49",-0.52500000000000002,-0.69115384615384612]
[6,28,2018,13,55,59,-0.63,-0.63,"2018-06-28T13:55:59",-0.54,-0.69576923076923058]
[6,28,2018,13,56,9,-0.63,-0.63,"2018-06-28T13:56:09",-0.57500000000000007,-0.70384615384615357]
[6,28,2018,13,56,19,-0.72,-0.72,"2018-06-28T13:56:19",-0.59500000000000008,-0.71307692307692294]
[6,28,2018,13,56,29,-0.72,-0.72,"2018-06-28T13:56:29",-0.625,-0.71884615384615358]
[6,28,2018,13,56,39,-0.69000000000000006,-0.69000000000000006,"2018-06-28T13:56:39",-0.65,-0.71884615384615358]
[6,28,2018,13,56,49,-0.84000000000000008,-0.84000000000000008,"2018-06-28T13:56:49",-0.70500000000000007,-0.72000000000000008]
[6,28,2018,13,56,59,-0.75,-0.75,"2018-06-28T13:56:59",-0.72500000000000009,-0.71769230769230774]
[6,28,2018,13,57,9,-0.51,-0.51,"2018-06-28T13:57:09",-0.70499999999999996,-0.70615384615384624]
[6,28,2018,13,57,19,-0.60000000000000009,-0.60000000000000009,"2018-06-28T13:57:19",-0.68499999999999994,-0.69576923076923092]
[6,28,2018,13,57,29,-0.54,-0.54,"2018-06-28T13:57:29",-0.65500000000000003,-0.6807692307692309]
[6,28,2018,13,57,39,-0.54,-0.54,"2018-06-28T13:57:39",-0.63,-0.66692307692307695]
[6,28,2018,13,57,49,-0.24,-0.24,"2018-06-28T13:57:49",-0.53000000000000014,-0.6449999999999998]
[6,28,2018,13,57,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:57:59",-0.4300000000000001,-0.63]
[6,28,2018,13,58,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T13:58:09",-0.37000000000000005,-0.61269230769230776]
[6,28,2018,13,58,19,-0.12,-0.12,"2018-06-28T13:58:19",-0.29000000000000004,-0.591923076923077]
[6,28,2018,13,58,29,-0.12,-0.12,"2018-06-28T13:58:29",-0.22000000000000006,-0.56307692307692303]
[6,28,2018,13,58,39,-0.06,-0.06,"2018-06-28T13:58:39",-0.14000000000000001,-0.52384615384615374]
[6,28,2018,13,58,49,-0.12,-0.12,"2018-06-28T13:58:49",-0.12000000000000001,-0.48576923076923068]
[6,28,2018,13,59,9,-0.33,-0.33,"2018-06-28T13:59:09",-0.16500000000000001,-0.45576923076923059]
[6,28,2018,13,59,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T13:59:49",-0.29500000000000004,-0.42115384615384627]
[6,28,2018,14,0,39,-0.18,-0.18,"2018-06-28T14:00:39",-0.125,-0.32192307692307687]
[6,28,2018,14,1,39,-0.03,-0.03,"2018-06-28T14:01:39",-0.17500000000000002,-0.20423076923076924]
[6,28,2018,14,2,29,-0.09,-0.09,"2018-06-28T14:02:29",-0.02,-0.14538461538461539]
[6,28,2018,14,3,19,-0.09,-0.09,"2018-06-28T14:03:19",-9.9999999999999992E-2,-0.13961538461538461]
[6,28,2018,14,4,19,0.03,0.03,"2018-06-28T14:04:19",-0.11000000000000003,-9.9230769230769261E-2]
[6,28,2018,14,5,9,-0.06,-0.06,"2018-06-28T14:05:09",5.0000000000000001E-3,-7.5000000000000011E-2]
[6,28,2018,14,6,9,0,0,"2018-06-28T14:06:09",-0.02,-5.5384615384615379E-2]
[6,28,2018,14,6,59,-0.03,-0.03,"2018-06-28T14:06:59",-2.4999999999999998E-2,-5.0769230769230782E-2]
[6,28,2018,14,7,49,-0.33,-0.33,"2018-06-28T14:07:49",-0.16,-6.807692307692309E-2]
[6,28,2018,14,7,59,-0.36,-0.36,"2018-06-28T14:07:59",-0.215,-7.6153846153846155E-2]
[6,28,2018,14,8,49,-0.27,-0.27,"2018-06-28T14:08:49",-0.41,-0.14307692307692307]
[6,28,2018,14,9,39,-0.24,-0.24,"2018-06-28T14:09:39",-0.24,{"$f":"AVERAGE(G2040:G2065)","v":-0.18346153846153848}]
[6,28,2018,14,10,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T14:10:39",-0.28000000000000003,-0.2457692307692308]
[6,28,2018,14,11,29,-0.48,-0.48,"2018-06-28T14:11:29",-0.40500000000000003,-0.31846153846153852]
[6,28,2018,14,12,29,-0.24,-0.24,"2018-06-28T14:12:29",-0.27999999999999997,-0.32076923076923081]
[6,28,2018,14,13,19,-0.39,-0.39,"2018-06-28T14:13:19",-0.375,-0.32423076923076927]
[6,28,2018,14,13,59,-0.09,-0.09,"2018-06-28T14:13:59",-0.29000000000000009,-0.32423076923076916]
[6,28,2018,14,14,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T14:14:59",-9.0000000000000011E-2,-0.28038461538461534]
[6,28,2018,14,15,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T14:15:49",-0.15,-0.22730769230769227]
[6,28,2018,14,16,49,-0.33,-0.33,"2018-06-28T14:16:49",-0.30000000000000004,-0.23192307692307693]
[6,28,2018,14,17,39,-0.36,-0.36,"2018-06-28T14:17:39",-0.32000000000000006,-0.21576923076923074]
[6,28,2018,14,18,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T14:18:29",-0.45999999999999996,-0.26884615384615385]
[6,28,2018,14,18,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T14:18:39",-0.47000000000000003,-0.28153846153846152]
[6,28,2018,14,19,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T14:19:29",-0.29500000000000004,-0.31500000000000006]
[6,28,2018,14,20,19,-0.27,-0.27,"2018-06-28T14:20:19",-0.28000000000000003,{"$f":"AVERAGE(G2104:G2129)","v":-0.33461538461538454}]
[6,28,2018,14,21,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T14:21:19",-0.21999999999999997,-0.31384615384615372]
[6,28,2018,14,22,9,-0.12,-0.12,"2018-06-28T14:22:09",-0.14000000000000001,-0.27000000000000007]
[6,28,2018,14,23,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T14:23:09",-0.19000000000000003,-0.21692307692307702]
[6,28,2018,14,23,59,-0.24,-0.24,"2018-06-28T14:23:59",-0.22,-0.2076923076923077]
[6,28,2018,14,24,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T14:24:49",-0.27,-0.20769230769230765]
[6,28,2018,14,25,49,-0.27,-0.27,"2018-06-28T14:25:49",-0.28000000000000003,-0.22730769230769232]
[6,28,2018,14,26,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T14:26:39",-0.24,-0.24230769230769234]
[6,28,2018,14,27,29,-0.09,-0.09,"2018-06-28T14:27:29",-0.14499999999999999,-0.2330769230769231]
[6,28,2018,14,28,19,-0.12,-0.12,"2018-06-28T14:28:19",-0.12,-0.21230769230769236]
[6,28,2018,14,29,9,-0.36,-0.36,"2018-06-28T14:29:09",-0.24500000000000002,-0.21115384615384619]
[6,28,2018,14,29,19,-0.33,-0.33,"2018-06-28T14:29:19",-0.28000000000000003,-0.21115384615384619]
[6,28,2018,14,30,9,-0.24,-0.24,"2018-06-28T14:30:09",-0.315,-0.2192307692307692]
[6,28,2018,14,30,59,-0.36,-0.36,"2018-06-28T14:30:59",-0.28499999999999998,{"$f":"AVERAGE(G2168:G2193)","v":-0.23076923076923078}]
[6,28,2018,14,31,59,-0.27,-0.27,"2018-06-28T14:31:59",-0.34500000000000003,-0.28038461538461534]
[6,28,2018,14,32,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T14:32:49",-0.29500000000000004,-0.31153846153846154]
[6,28,2018,14,33,49,-0.33,-0.33,"2018-06-28T14:33:49",-0.27,-0.30115384615384605]
[6,28,2018,14,34,39,-0.33,-0.33,"2018-06-28T14:34:39",-0.32000000000000006,-0.30807692307692303]
[6,28,2018,14,35,29,-0.24,-0.24,"2018-06-28T14:35:29",-0.22499999999999998,-0.28615384615384615]
[6,28,2018,14,36,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T14:36:29",-0.36999999999999994,-0.29538461538461536]
[6,28,2018,14,37,19,-0.33,-0.33,"2018-06-28T14:37:19",-0.375,-0.30576923076923079]
[6,28,2018,14,38,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T14:38:09",-0.33,-0.31846153846153852]
[6,28,2018,14,39,9,-0.48,-0.48,"2018-06-28T14:39:09",-0.38000000000000006,-0.33807692307692305]
[6,28,2018,14,39,59,-0.18,-0.18,"2018-06-28T14:39:59",-0.33499999999999996,-0.3553846153846153]
[6,28,2018,14,40,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T14:40:09",-0.28000000000000003,-0.34846153846153843]
[6,28,2018,14,40,59,-0.12,-0.12,"2018-06-28T14:40:59",-0.14500000000000002,-0.29538461538461547]
[6,28,2018,14,41,59,-0.09,-0.09,"2018-06-28T14:41:59",-9.4999999999999987E-2,-0.2376923076923077]
[6,28,2018,14,42,39,-0.18,-0.18,"2018-06-28T14:42:39",-0.13,-0.21346153846153848]
[6,28,2018,14,43,29,-0.09,-0.09,"2018-06-28T14:43:29",-0.16499999999999998,-0.16730769230769232]
[6,28,2018,14,44,29,-0.12,-0.12,"2018-06-28T14:44:29",-0.14499999999999999,-0.13615384615384618]
[6,28,2018,14,45,19,-0.06,-0.06,"2018-06-28T14:45:19",-6.4999999999999988E-2,-0.11884615384615384]
[6,28,2018,14,46,9,-0.03,-0.03,"2018-06-28T14:46:09",-3.4999999999999996E-2,-0.10615384615384614]
[6,28,2018,14,47,9,-0.03,-0.03,"2018-06-28T14:47:09",-2.4999999999999998E-2,-7.9615384615384616E-2]
[6,28,2018,14,47,59,-0.09,-0.09,"2018-06-28T14:47:59",-9.4999999999999987E-2,-7.1538461538461565E-2]
[6,28,2018,14,48,49,-0.03,-0.03,"2018-06-28T14:48:49",-0.06,-5.3076923076923091E-2]
[6,28,2018,14,49,49,0,0,"2018-06-28T14:49:49",0.01,-4.0384615384615387E-2]
[6,28,2018,14,50,39,0.03,0.03,"2018-06-28T14:50:39",5.0000000000000001E-3,-3.2307692307692308E-2]
[6,28,2018,14,50,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T14:50:49",-2.0000000000000004E-2,-3.8076923076923078E-2]
[6,28,2018,14,51,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T14:51:39",-0.16500000000000001,-6.1153846153846149E-2]
[6,28,2018,14,52,29,0,0,"2018-06-28T14:52:29",-7.5000000000000011E-2,-5.1923076923076926E-2]
[6,28,2018,14,53,29,-0.06,-0.06,"2018-06-28T14:53:29",-0.04,-5.4230769230769242E-2]
[6,28,2018,14,54,19,0,0,"2018-06-28T14:54:19",-0.02,-5.7692307692307709E-2]
[6,28,2018,14,55,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T14:55:09",-0.06,-6.6923076923076932E-2]
[6,28,2018,14,56,9,-0.51,-0.51,"2018-06-28T14:56:09",-0.35499999999999998,-0.11307692307692306]
[6,28,2018,14,56,49,-0.33,-0.33,"2018-06-28T14:56:49",-0.45999999999999996,-0.17653846153846153]
[6,28,2018,14,57,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T14:57:49",-0.43,-0.2665384615384615]
[6,28,2018,14,58,39,-0.57000000000000006,-0.57000000000000006,"2018-06-28T14:58:39",-0.52500000000000002,-0.36807692307692308]
[6,28,2018,14,59,29,-0.66,-0.66,"2018-06-28T14:59:29",-0.65500000000000014,-0.48346153846153839]
[6,28,2018,15,0,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T15:00:29",-0.53500000000000003,-0.52500000000000002]
[6,28,2018,15,1,19,-0.27,-0.27,"2018-06-28T15:01:19",-0.32,-0.49730769230769234]
[6,28,2018,15,1,29,-0.27,-0.27,"2018-06-28T15:01:29",-0.28999999999999998,-0.49269230769230771]
[6,28,2018,15,2,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T15:02:19",-0.245,-0.45230769230769224]
[6,28,2018,15,3,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T15:03:09",-0.255,-0.39000000000000007]
[6,28,2018,15,4,9,-0.36,-0.36,"2018-06-28T15:04:09",-0.34,-0.31846153846153852]
[6,28,2018,15,4,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T15:04:59",-0.33500000000000002,-0.28846153846153855]
[6,28,2018,15,5,49,-0.42000000000000004,-0.42000000000000004,"2018-06-28T15:05:49",-0.31000000000000005,-0.29884615384615382]
[6,28,2018,15,6,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T15:06:49",-0.40499999999999997,-0.33807692307692305]
[6,28,2018,15,7,39,-0.24,-0.24,"2018-06-28T15:07:39",-0.27500000000000002,-0.33461538461538459]
[6,28,2018,15,8,39,-0.12,-0.12,"2018-06-28T15:08:39",-0.17,-0.29423076923076918]
[6,28,2018,15,9,29,-0.09,-0.09,"2018-06-28T15:09:29",-0.105,-0.25269230769230766]
[6,28,2018,15,10,19,-0.06,-0.06,"2018-06-28T15:10:19",{"$f":"AVERAGE(G2424:G2429)","v":-8.5000000000000006E-2},-0.20538461538461533]
[6,28,2018,15,11,9,-0.24,-0.24,"2018-06-28T15:11:09",-0.14499999999999999,-0.15807692307692309]
[6,28,2018,15,11,59,-0.12,-0.12,"2018-06-28T15:11:59",-0.22500000000000001,-0.14884615384615388]
[6,28,2018,15,12,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T15:12:49",-0.17999999999999997,-0.15115384615384617]
[6,28,2018,15,12,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T15:12:59",-0.21,-0.15807692307692309]
[6,28,2018,15,13,49,-0.48,-0.48,"2018-06-28T15:13:49",-0.38500000000000006,-0.21576923076923082]
[6,28,2018,15,14,49,-0.51,-0.51,"2018-06-28T15:14:49",-0.51500000000000001,-0.31615384615384617]
[6,28,2018,15,15,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T15:15:39",-0.39500000000000002,-0.34846153846153849]
[6,28,2018,15,16,29,-0.24,-0.24,"2018-06-28T15:16:29",-0.27999999999999997,-0.36230769230769233]
[6,28,2018,15,17,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T15:17:29",-0.155,-0.3438461538461538]
[6,28,2018,15,18,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T15:18:19",-0.20000000000000004,-0.29769230769230764]
[6,28,2018,15,19,19,-0.12,-0.12,"2018-06-28T15:19:19",-0.16500000000000001,-0.22153846153846152]
[6,28,2018,15,20,9,-0.03,-0.03,"2018-06-28T15:20:09",-9.4999999999999987E-2,-0.1684615384615385]
[6,28,2018,15,20,59,-0.12,-0.12,"2018-06-28T15:20:59",{"$f":"AVERAGE(G2488:G2493)","v":-6.5000000000000002E-2},-0.13961538461538459]
[6,28,2018,15,21,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T15:21:59",-0.22499999999999998,-0.14999999999999997]
[6,28,2018,15,22,49,-0.42000000000000004,-0.42000000000000004,"2018-06-28T15:22:49",-0.25500000000000006,-0.16384615384615386]
[6,28,2018,15,23,39,-0.33,-0.33,"2018-06-28T15:23:39",-0.38500000000000006,-0.20653846153846153]
[6,28,2018,15,23,49,-0.18,-0.18,"2018-06-28T15:23:49",-0.34500000000000003,-0.21230769230769228]
[6,28,2018,15,24,49,-0.24,-0.24,"2018-06-28T15:24:49",-0.23,-0.24692307692307691]
[6,28,2018,15,25,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T15:25:29",-0.26,-0.26884615384615385]
[6,28,2018,15,26,19,-0.27,-0.27,"2018-06-28T15:26:19",-0.29000000000000004,-0.28038461538461534]
[6,28,2018,15,27,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T15:27:09",-0.29000000000000004,-0.28615384615384609]
[6,28,2018,15,28,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T15:28:09",-0.29000000000000004,-0.27346153846153848]
[6,28,2018,15,28,59,-0.27,-0.27,"2018-06-28T15:28:59",-0.29000000000000004,-0.28499999999999992]
[6,28,2018,15,29,59,-0.18,-0.18,"2018-06-28T15:29:59",-0.22999999999999998,-0.27576923076923071]
[6,28,2018,15,30,49,-0.09,-0.09,"2018-06-28T15:30:49",-0.15,-0.24807692307692306]
[6,28,2018,15,31,39,-0.09,-0.09,"2018-06-28T15:31:39",{"$f":"AVERAGE(G2552:G2557)","v":-0.08},-0.20769230769230759]
[6,28,2018,15,32,39,-0.06,-0.06,"2018-06-28T15:32:39",-6.9999999999999993E-2,-0.1557692307692308]
[6,28,2018,15,33,29,0,0,"2018-06-28T15:33:29",-0.03,-0.105]
[6,28,2018,15,34,19,0.12,0.12,"2018-06-28T15:34:19",6.5000000000000002E-2,-4.8461538461538473E-2]
[6,28,2018,15,34,29,0.06,0.06,"2018-06-28T15:34:29",7.4999999999999997E-2,-3.9230769230769229E-2]
[6,28,2018,15,35,19,-0.24,-0.24,"2018-06-28T15:35:19",-8.5000000000000006E-2,-3.5769230769230775E-2]
[6,28,2018,15,36,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T15:36:19",-0.28499999999999998,-8.4230769230769234E-2]
[6,28,2018,15,37,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T15:37:09",-0.32500000000000001,-0.13730769230769233]
[6,28,2018,15,37,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T15:37:59",-0.26,-0.18230769230769234]
[6,28,2018,15,38,59,-0.39,-0.39,"2018-06-28T15:38:59",-0.30499999999999999,-0.27230769230769231]
[6,28,2018,15,39,39,-0.24,-0.24,"2018-06-28T15:39:39",-0.29000000000000004,-0.28846153846153844]
[6,28,2018,15,40,29,-0.27,-0.27,"2018-06-28T15:40:29",-0.255,-0.2838461538461538]
[6,28,2018,15,41,29,-0.27,-0.27,"2018-06-28T15:41:29",-0.26,-0.26884615384615385]
[6,28,2018,15,42,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T15:42:19",{"$f":"AVERAGE(G2616:G2621)","v":-0.30499999999999999},-0.2803846153846154]
[6,28,2018,15,43,19,-0.09,-0.09,"2018-06-28T15:43:19",-0.17500000000000002,-0.25038461538461543]
[6,28,2018,15,44,9,-0.18,-0.18,"2018-06-28T15:44:09",-0.14500000000000002,-0.23076923076923073]
[6,28,2018,15,44,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T15:44:59",-0.245,-0.22846153846153844]
[6,28,2018,15,45,9,-0.24,-0.24,"2018-06-28T15:45:09",-0.255,-0.22730769230769227]
[6,28,2018,15,45,59,-0.24,-0.24,"2018-06-28T15:45:59",-0.26500000000000001,-0.22961538461538464]
[6,28,2018,15,46,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T15:46:59",-0.27500000000000002,-0.22500000000000003]
[6,28,2018,15,47,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T15:47:49",-0.32000000000000006,-0.2630769230769231]
[6,28,2018,15,48,39,-0.24,-0.24,"2018-06-28T15:48:39",-0.27,-0.27807692307692311]
[6,28,2018,15,49,39,-0.09,-0.09,"2018-06-28T15:49:39",-0.16500000000000001,-0.25730769230769229]
[6,28,2018,15,50,29,-0.03,-0.03,"2018-06-28T15:50:29",-5.5000000000000014E-2,-0.21461538461538465]
[6,28,2018,15,51,19,-0.09,-0.09,"2018-06-28T15:51:19",-0.04,-0.1684615384615385]
[6,28,2018,15,52,19,-0.24,-0.24,{"$f":"DATE(C2681,A2681,B2681)+TIME(D2681,E2681,F2681)","v":"2018-06-28T15:52:19"},-0.18999999999999997,-0.13846153846153841]
[6,28,2018,15,53,9,-0.12,-0.12,"2018-06-28T15:53:09",-0.19000000000000003,-0.12692307692307694]
[6,28,2018,15,53,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T15:53:29",-0.20000000000000004,-0.13153846153846155]
[6,28,2018,15,54,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T15:54:49",-0.20000000000000004,-0.17076923076923076]
[6,28,2018,15,55,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T15:55:39",-0.13,-0.18692307692307691]
[6,28,2018,15,55,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T15:55:49",-0.14000000000000001,-0.19038461538461535]
[6,28,2018,15,56,39,-0.27,-0.27,"2018-06-28T15:56:39",-0.26500000000000001,-0.20423076923076919]
[6,28,2018,15,57,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T15:57:39",-0.30000000000000004,-0.2307692307692307]
[6,28,2018,15,58,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T15:58:29",-0.39500000000000002,-0.2630769230769231]
[6,28,2018,15,59,19,-0.57000000000000006,-0.57000000000000006,"2018-06-28T15:59:19",-0.54,-0.33461538461538465]
[6,28,2018,16,0,19,-0.27,-0.27,"2018-06-28T16:00:19",-0.36999999999999994,-0.38423076923076915]
[6,28,2018,16,1,9,-0.06,-0.06,"2018-06-28T16:01:09",-0.18000000000000002,-0.36230769230769233]
[6,28,2018,16,1,59,0.06,0.06,"2018-06-28T16:01:59",-6.9999999999999993E-2,-0.31730769230769224]
[6,28,2018,16,2,59,0,0,{"$f":"DATE(C2745,A2745,B2745)+TIME(D2745,E2745,F2745)","v":"2018-06-28T16:02:59"},0.105,-0.19269230769230769]
[6,28,2018,16,3,49,-0.09,-0.09,"2018-06-28T16:03:49",-0.08,-0.10269230769230769]
[6,28,2018,16,4,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T16:04:49",-0.06,-4.4999999999999998E-2]
[6,28,2018,16,5,39,-0.27,-0.27,"2018-06-28T16:05:39",-0.15,-4.3846153846153854E-2]
[6,28,2018,16,6,29,-0.03,-0.03,"2018-06-28T16:06:29",-0.16500000000000001,-7.0384615384615379E-2]
[6,28,2018,16,6,39,-0.03,-0.03,"2018-06-28T16:06:39",-0.125,-7.8461538461538444E-2]
[6,28,2018,16,7,39,-0.06,-0.06,"2018-06-28T16:07:39",-0.04,-9.1153846153846113E-2]
[6,28,2018,16,8,9,0.03,0.03,"2018-06-28T16:08:09",-2.4999999999999998E-2,-8.1923076923076904E-2]
[6,28,2018,16,9,9,-0.03,-0.03,"2018-06-28T16:09:09",-2.4999999999999998E-2,-7.3846153846153867E-2]
[6,28,2018,16,9,59,0,0,"2018-06-28T16:09:59",2.4999999999999998E-2,-3.8076923076923085E-2]
[6,28,2018,16,10,59,0.15000000000000002,0.15000000000000002,"2018-06-28T16:10:59",4.5000000000000005E-2,1.1538461538461485E-3]
[6,28,2018,16,11,49,0.15000000000000002,0.15000000000000002,"2018-06-28T16:11:49",0.19499999999999998,4.7307692307692308E-2]
[6,28,2018,16,12,39,0,0,"2018-06-28T16:12:39",6.5000000000000002E-2,6.1153846153846163E-2]
[6,28,2018,16,13,39,-0.15000000000000002,-0.15000000000000002,{"$f":"DATE(C2809,A2809,B2809)+TIME(D2809,E2809,F2809)","v":"2018-06-28T16:13:39"},-1.0000000000000004E-2,6.3461538461538458E-2]
[6,28,2018,16,14,29,-0.18,-0.18,"2018-06-28T16:14:29",-0.20499999999999999,1.7307692307692323E-2]
[6,28,2018,16,15,29,-0.18,-0.18,"2018-06-28T16:15:29",-0.17,-4.3846153846153854E-2]
[6,28,2018,16,16,19,-0.09,-0.09,"2018-06-28T16:16:19",-0.125,-0.10038461538461538]
[6,28,2018,16,17,9,-0.18,-0.18,"2018-06-28T16:17:09",-0.13500000000000001,-0.13615384615384615]
[6,28,2018,16,17,19,-0.12,-0.12,"2018-06-28T16:17:19",-0.13999999999999999,-0.14423076923076922]
[6,28,2018,16,18,9,-0.06,-0.06,"2018-06-28T16:18:09",-0.12,-0.14769230769230773]
[6,28,2018,16,18,59,-0.03,-0.03,"2018-06-28T16:18:59",-4.5000000000000005E-2,-0.11769230769230771]
[6,28,2018,16,19,59,-0.09,-0.09,"2018-06-28T16:19:59",-6.9999999999999993E-2,-9.5769230769230745E-2]
[6,28,2018,16,20,49,-0.33,-0.33,"2018-06-28T16:20:49",-0.18000000000000002,-0.11423076923076926]
[6,28,2018,16,21,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T16:21:49",-0.21999999999999997,-0.12923076923076923]
[6,28,2018,16,22,29,-0.03,-0.03,"2018-06-28T16:22:29",-0.11000000000000003,-0.12346153846153846]
[6,28,2018,16,23,19,-0.24,-0.24,"2018-06-28T16:23:19",-0.12,-0.14192307692307693]
[6,28,2018,16,24,19,-0.44999999999999996,-0.44999999999999996,{"$f":"DATE(C2873,A2873,B2873)+TIME(D2873,E2873,F2873)","v":"2018-06-28T16:24:19"},-0.39999999999999997,-0.21807692307692311]
[6,28,2018,16,25,9,-0.51,-0.51,"2018-06-28T16:25:09",-0.50499999999999989,-0.27923076923076923]
[6,28,2018,16,25,59,-0.44999999999999996,-0.44999999999999996,"2018-06-28T16:25:59",-0.45,-0.31846153846153846]
[6,28,2018,16,26,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T16:26:59",-0.44500000000000001,-0.40269230769230774]
[6,28,2018,16,27,49,-0.24,-0.24,"2018-06-28T16:27:49",-0.27,-0.41769230769230775]
[6,28,2018,16,27,59,-0.24,-0.24,"2018-06-28T16:27:59",-0.26,-0.41307692307692317]
[6,28,2018,16,28,49,-0.27,-0.27,"2018-06-28T16:28:49",-0.28000000000000003,-0.38192307692307698]
[6,28,2018,16,29,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T16:29:39",-0.33,-0.34961538461538461]
[6,28,2018,16,30,39,-0.48,-0.48,"2018-06-28T16:30:39",-0.47500000000000003,-0.35538461538461541]
[6,28,2018,16,31,29,-0.54,-0.54,"2018-06-28T16:31:29",-0.51500000000000001,-0.37730769230769223]
[6,28,2018,16,32,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T16:32:29",-0.41,-0.4153846153846153]
[6,28,2018,16,33,19,-0.57000000000000006,-0.57000000000000006,"2018-06-28T16:33:19",-0.52,-0.46153846153846156]
[6,28,2018,16,34,9,-0.57000000000000006,-0.57000000000000006,"2018-06-28T16:34:09",-0.49499999999999994,-0.48115384615384615]
[6,28,2018,16,35,9,-0.27,-0.27,"2018-06-28T16:35:09",-0.42999999999999994,-0.46961538461538466]
[6,28,2018,16,35,59,-0.33,-0.33,"2018-06-28T16:35:59",-0.30000000000000004,-0.43038461538461542]
[6,28,2018,16,36,19,-0.33,-0.33,"2018-06-28T16:36:19",-0.32000000000000006,-0.42230769230769238]
[6,28,2018,16,37,39,-0.27,-0.27,"2018-06-28T16:37:39",-0.35000000000000003,-0.38076923076923069]
[6,28,2018,16,38,29,-0.24,-0.24,"2018-06-28T16:38:29",-0.215,-0.32769230769230784]
[6,28,2018,16,38,39,-0.27,-0.27,"2018-06-28T16:38:39",-0.215,-0.31500000000000011]
[6,28,2018,16,39,29,-0.12,-0.12,"2018-06-28T16:39:29",-0.20499999999999999,-0.27576923076923082]
[6,28,2018,16,40,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T16:40:19",-0.125,-0.24115384615384616]
[6,28,2018,16,41,19,-0.09,-0.09,"2018-06-28T16:41:19",-0.08,-0.1846153846153846]
[6,28,2018,16,42,9,-0.12,-0.12,"2018-06-28T16:42:09",-0.105,-0.1419230769230769]
[6,28,2018,16,43,9,-0.24,-0.24,"2018-06-28T16:43:09",-0.18500000000000003,-0.13269230769230772]
[6,28,2018,16,43,59,-0.18,-0.18,"2018-06-28T16:43:59",-0.17500000000000002,-0.13384615384615384]
[6,28,2018,16,44,49,-0.03,-0.03,"2018-06-28T16:44:49",-0.12,-0.1292307692307692]
[6,28,2018,16,45,49,-0.27,-0.27,"2018-06-28T16:45:49",-0.14500000000000002,-0.14423076923076922]
[6,28,2018,16,46,39,-0.27,-0.27,"2018-06-28T16:46:39",-0.315,-0.18461538461538457]
[6,28,2018,16,47,29,-0.27,-0.27,"2018-06-28T16:47:29",-0.22500000000000001,-0.18923076923076923]
[6,28,2018,16,48,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T16:48:29",-0.33,-0.22615384615384615]
[6,28,2018,16,49,19,-0.18,-0.18,"2018-06-28T16:49:19",-0.19999999999999998,-0.24692307692307688]
[6,28,2018,16,49,29,-0.27,-0.27,"2018-06-28T16:49:29",-0.19500000000000003,-0.25615384615384618]
[6,28,2018,16,50,29,-0.39,-0.39,"2018-06-28T16:50:29",-0.32000000000000006,-0.27576923076923071]
[6,28,2018,16,50,59,-0.44999999999999996,-0.44999999999999996,"2018-06-28T16:50:59",-0.38500000000000006,-0.28153846153846152]
[6,28,2018,16,51,59,-0.39,-0.39,"2018-06-28T16:51:59",-0.38500000000000001,-0.31846153846153852]
[6,28,2018,16,52,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T16:52:49",-0.36999999999999994,-0.32307692307692309]
[6,28,2018,16,53,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T16:53:39",-0.30500000000000005,-0.34730769230769237]
[6,28,2018,16,54,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T16:54:39",-0.30500000000000005,-0.34846153846153849]
[6,28,2018,16,55,29,-0.27,-0.27,"2018-06-28T16:55:29",-0.32500000000000001,-0.33807692307692305]
[6,28,2018,16,56,29,0.09,0.09,"2018-06-28T16:56:29",1.9999999999999993E-2,-0.24230769230769234]
[6,28,2018,16,57,19,-0.03,-0.03,"2018-06-28T16:57:19",4.5000000000000005E-2,-0.1684615384615385]
[6,28,2018,16,58,9,-0.27,-0.27,"2018-06-28T16:58:09",-0.16500000000000001,-0.14769230769230773]
[6,28,2018,16,59,9,-0.12,-0.12,"2018-06-28T16:59:09",-0.155,-0.10961538461538464]
[6,28,2018,16,59,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T16:59:59",-0.19500000000000003,-9.5769230769230773E-2]
[6,28,2018,17,0,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T17:00:09",-0.22500000000000001,-0.10730769230769231]
[6,28,2018,17,0,59,0.06,0.06,"2018-06-28T17:00:59",-0.17,-0.14653846153846153]
[6,28,2018,17,1,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T17:01:49",-6.0000000000000005E-2,-0.16500000000000004]
[6,28,2018,17,2,49,-0.24,-0.24,"2018-06-28T17:02:49",-0.155,-0.14884615384615385]
[6,28,2018,17,3,39,-0.24,-0.24,"2018-06-28T17:03:39",-0.22499999999999998,-0.1696153846153847]
[6,28,2018,17,4,29,-0.36,-0.36,"2018-06-28T17:04:29",-0.34499999999999997,-0.19269230769230775]
[6,28,2018,17,5,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T17:05:39",-0.40500000000000003,-0.27230769230769225]
[6,28,2018,17,6,9,-0.27,-0.27,"2018-06-28T17:06:09",-0.33500000000000002,-0.28846153846153838]
[6,28,2018,17,7,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T17:07:09",-0.19999999999999998,-0.29884615384615382]
[6,28,2018,17,7,59,-0.12,-0.12,"2018-06-28T17:07:59",-0.17,-0.28730769230769232]
[6,28,2018,17,8,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T17:08:49",-0.26999999999999996,-0.27461538461538465]
[6,28,2018,17,9,49,-0.54,-0.54,"2018-06-28T17:09:49",-0.38999999999999996,-0.27230769230769231]
[6,28,2018,17,10,39,-0.36,-0.36,"2018-06-28T17:10:39",-0.42499999999999999,-0.29307692307692307]
[6,28,2018,17,11,29,-0.24,-0.24,"2018-06-28T17:11:29",-0.19999999999999998,-0.28846153846153849]
[6,28,2018,17,11,39,-0.18,-0.18,"2018-06-28T17:11:39",-0.17,-0.28615384615384615]
[6,28,2018,17,12,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T17:12:29",-0.27999999999999997,-0.31615384615384617]
[6,28,2018,17,13,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T17:13:29",-0.14500000000000002,-0.26884615384615385]
[6,28,2018,17,14,19,-0.48,-0.48,"2018-06-28T17:14:19",-0.39999999999999997,-0.26999999999999996]
[6,28,2018,17,15,9,-0.27,-0.27,"2018-06-28T17:15:09",-0.41,-0.28038461538461529]
[6,28,2018,17,16,9,-0.24,-0.24,"2018-06-28T17:16:09",-0.3,-0.30346153846153839]
[6,28,2018,17,16,59,-0.24,-0.24,"2018-06-28T17:16:59",-0.22999999999999998,-0.29538461538461536]
[6,28,2018,17,17,59,-0.27,-0.27,"2018-06-28T17:17:59",-0.30000000000000004,-0.32769230769230767]
[6,28,2018,17,18,49,-0.51,-0.51,"2018-06-28T17:18:49",-0.33,-0.30461538461538462]
[6,28,2018,17,19,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T17:19:09",-0.39500000000000002,-0.30461538461538462]
[6,28,2018,17,20,29,-0.27,-0.27,"2018-06-28T17:20:29",-0.29499999999999998,-0.31846153846153846]
[6,28,2018,17,21,19,-0.27,-0.27,"2018-06-28T17:21:19",-0.26500000000000001,-0.32538461538461527]
[6,28,2018,17,22,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T17:22:09",-0.35000000000000003,-0.33692307692307683]
[6,28,2018,17,22,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T17:22:19",-0.38000000000000006,-0.34384615384615375]
[6,28,2018,17,23,9,-0.33,-0.33,"2018-06-28T17:23:09",-0.42499999999999999,-0.35884615384615376]
[6,28,2018,17,24,9,-0.54,-0.54,"2018-06-28T17:24:09",-0.39500000000000002,-0.35076923076923083]
[6,28,2018,17,24,59,-0.51,-0.51,"2018-06-28T17:24:59",-0.49499999999999994,-0.39346153846153853]
[6,28,2018,17,25,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T17:25:49",-0.35999999999999993,-0.40384615384615397]
[6,28,2018,17,26,49,-0.48,-0.48,"2018-06-28T17:26:49",-0.36000000000000004,-0.39461538461538459]
[6,28,2018,17,27,39,-0.44999999999999996,-0.44999999999999996,"2018-06-28T17:27:39",-0.5,-0.41538461538461535]
[6,28,2018,17,28,39,-0.44999999999999996,-0.44999999999999996,"2018-06-28T17:28:39",-0.41500000000000004,-0.41192307692307695]
[6,28,2018,17,29,29,-0.36,-0.36,"2018-06-28T17:29:29",-0.42499999999999999,-0.40153846153846146]
[6,28,2018,17,30,19,-0.33,-0.33,"2018-06-28T17:30:19",-0.35000000000000003,-0.41538461538461541]
[6,28,2018,17,31,19,-0.48,-0.48,"2018-06-28T17:31:19",-0.40499999999999997,-0.41423076923076929]
[6,28,2018,17,32,9,-0.24,-0.24,"2018-06-28T17:32:09",-0.36999999999999994,-0.38884615384615384]
[6,28,2018,17,32,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T17:32:59",-0.16500000000000001,-0.33692307692307694]
[6,28,2018,17,33,19,-0.09,-0.09,"2018-06-28T17:33:19",-0.12000000000000001,-0.30692307692307697]
[6,28,2018,17,33,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T17:33:49",-0.12000000000000001,-0.27807692307692311]
[6,28,2018,17,34,49,0,0,"2018-06-28T17:34:49",-0.18000000000000002,-0.24115384615384622]
[6,28,2018,17,35,39,0.03,0.03,"2018-06-28T17:35:39",-5.0000000000000001E-3,-0.16038461538461538]
[6,28,2018,17,36,29,-0.12,-0.12,"2018-06-28T17:36:29",-6.9999999999999993E-2,-0.11076923076923073]
[6,28,2018,17,37,29,-0.24,-0.24,"2018-06-28T17:37:29",-0.16500000000000001,-0.11769230769230771]
[6,28,2018,17,38,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T17:38:19",-0.25000000000000006,-0.13961538461538461]
[6,28,2018,17,39,9,-0.18,-0.18,"2018-06-28T17:39:09",-0.27,-0.15576923076923077]
[6,28,2018,17,40,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T17:40:09",-0.19000000000000003,-0.19499999999999998]
[6,28,2018,17,40,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T17:40:59",-0.18000000000000002,-0.21230769230769234]
[6,28,2018,17,41,59,-0.39,-0.39,"2018-06-28T17:41:59",-0.28000000000000003,-0.23538461538461539]
[6,28,2018,17,42,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T17:42:49",-0.375,-0.25961538461538453]
[6,28,2018,17,43,39,-0.27,-0.27,"2018-06-28T17:43:39",-0.255,-0.25846153846153841]
[6,28,2018,17,43,49,-0.39,-0.39,"2018-06-28T17:43:49",-0.28499999999999998,-0.2665384615384615]
[6,28,2018,17,44,39,-0.36,-0.36,"2018-06-28T17:44:39",-0.41999999999999993,-0.31615384615384612]
[6,28,2018,17,45,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T17:45:39",-0.45,-0.37153846153846148]
[6,28,2018,17,46,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T17:46:29",-0.26999999999999996,-0.35423076923076924]
[6,28,2018,17,47,19,-0.27,-0.27,"2018-06-28T17:47:19",-0.22500000000000001,-0.3323076923076923]
[6,28,2018,17,48,29,-0.33,-0.33,"2018-06-28T17:48:29",-0.30500000000000005,-0.32307692307692309]
[6,28,2018,17,48,59,-0.39,-0.39,"2018-06-28T17:48:59",-0.34500000000000003,-0.31961538461538463]
[6,28,2018,17,49,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T17:49:49",-0.47499999999999992,-0.3265384615384615]
[6,28,2018,17,50,49,-0.33,-0.33,"2018-06-28T17:50:49",-0.37999999999999995,-0.35192307692307695]
[6,28,2018,17,51,39,-0.24,-0.24,"2018-06-28T17:51:39",-0.28000000000000003,-0.36]
[6,28,2018,17,52,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T17:52:39",-0.16500000000000001,-0.32769230769230767]
[6,28,2018,17,53,29,0,0,"2018-06-28T17:53:29",-6.0000000000000005E-2,-0.26192307692307687]
[6,28,2018,17,54,19,-0.09,-0.09,"2018-06-28T17:54:19",-0.04,-0.17999999999999997]
[6,28,2018,17,54,29,-0.18,-0.18,"2018-06-28T17:54:29",-6.9999999999999993E-2,-0.17307692307692304]
[6,28,2018,17,55,19,-0.33,-0.33,"2018-06-28T17:55:19",-0.25500000000000006,-0.1546153846153846]
[6,28,2018,17,56,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T17:56:19",-0.30499999999999999,-0.16730769230769232]
[6,28,2018,17,57,9,-0.27,-0.27,"2018-06-28T17:57:09",-0.26,-0.19615384615384615]
[6,28,2018,17,57,59,-0.48,-0.48,"2018-06-28T17:57:59",-0.36000000000000004,-0.2630769230769231]
[6,28,2018,17,58,59,-0.44999999999999996,-0.44999999999999996,"2018-06-28T17:58:59",-0.42499999999999999,-0.33692307692307683]
[6,28,2018,17,59,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T17:59:49",-0.38999999999999996,-0.35307692307692307]
[6,28,2018,18,0,39,-0.24,-0.24,"2018-06-28T18:00:39",-0.215,-0.33692307692307699]
[6,28,2018,18,1,39,-0.48,-0.48,"2018-06-28T18:01:39",-0.435,-0.375]
[6,28,2018,18,1,59,-0.36,-0.36,"2018-06-28T18:01:59",-0.42499999999999999,-0.37846153846153846]
[6,28,2018,18,3,19,-0.33,-0.33,"2018-06-28T18:03:19",-0.38000000000000006,-0.36115384615384616]
[6,28,2018,18,4,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T18:04:09",-0.38499999999999995,-0.36461538461538462]
[6,28,2018,18,4,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T18:04:59",-0.34500000000000003,-0.38653846153846155]
[6,28,2018,18,5,9,-0.27,-0.27,"2018-06-28T18:05:09",-0.32,-0.38192307692307692]
[6,28,2018,18,5,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T18:05:59",-0.29000000000000004,-0.35307692307692318]
[6,28,2018,18,6,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T18:06:49",-0.30000000000000004,-0.33461538461538465]
[6,28,2018,18,7,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T18:07:49",-0.29000000000000004,-0.31730769230769229]
[6,28,2018,18,8,39,-0.33,-0.33,"2018-06-28T18:08:39",-0.31000000000000005,-0.30115384615384616]
[6,28,2018,18,9,39,-0.39,-0.39,"2018-06-28T18:09:39",-0.35000000000000003,-0.31038461538461548]
[6,28,2018,18,10,29,-0.51,-0.51,"2018-06-28T18:10:29",-0.43,-0.33692307692307694]
[6,28,2018,18,11,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T18:11:19",-0.47499999999999992,-0.37153846153846154]
[6,28,2018,18,12,19,-0.54,-0.54,"2018-06-28T18:12:19",-0.49000000000000005,-0.41653846153846164]
[6,28,2018,18,13,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T18:13:09",-0.47499999999999992,-0.4442307692307691]
[6,28,2018,18,14,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T18:14:09",-0.41500000000000004,-0.45807692307692299]
[6,28,2018,18,14,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T18:14:59",-0.38500000000000001,{"$f":"AVERAGE(G3512:G3537)","v":-0.44192307692307686}]
[6,28,2018,18,15,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T18:15:49",-0.34499999999999997,-0.4176923076923077]
[6,28,2018,18,15,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T18:15:59",-0.3,-0.4061538461538462]
[6,28,2018,18,17,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T18:17:09",-0.15,-0.3115384615384616]
[6,28,2018,18,17,29,-0.12,-0.12,"2018-06-28T18:17:29",-0.14000000000000001,-0.28730769230769237]
[6,28,2018,18,18,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T18:18:29",-0.27,-0.25384615384615389]
[6,28,2018,18,19,19,-0.27,-0.27,"2018-06-28T18:19:19",-0.245,-0.22615384615384612]
[6,28,2018,18,20,19,-0.24,-0.24,"2018-06-28T18:20:19",-0.25,-0.21461538461538468]
[6,28,2018,18,21,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T18:21:09",-0.3,-0.24692307692307697]
[6,28,2018,18,21,59,-0.18,-0.18,"2018-06-28T18:21:59",-0.26,-0.26884615384615385]
[6,28,2018,18,22,59,-0.18,-0.18,"2018-06-28T18:22:59",-0.20499999999999999,-0.24692307692307686]
[6,28,2018,18,23,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T18:23:49",-0.20000000000000004,-0.2434615384615384]
[6,28,2018,18,24,39,-0.36,-0.36,"2018-06-28T18:24:39",-0.33,-0.25961538461538464]
[6,28,2018,18,25,39,-0.27,-0.27,"2018-06-28T18:25:39",-0.25,{"$f":"AVERAGE(G3576:G3601)","v":-0.2457692307692308}]
[6,28,2018,18,26,29,-0.36,-0.36,"2018-06-28T18:26:29",-0.32,-0.26538461538461539]
[6,28,2018,18,26,39,-0.36,-0.36,"2018-06-28T18:26:39",-0.33499999999999996,-0.27115384615384613]
[6,28,2018,18,27,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T18:27:29",-0.38999999999999996,-0.30807692307692314]
[6,28,2018,18,28,19,-0.51,-0.51,"2018-06-28T18:28:19",-0.46500000000000002,-0.35423076923076924]
[6,28,2018,18,29,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T18:29:19",-0.38999999999999996,-0.37269230769230777]
[6,28,2018,18,30,9,-0.60000000000000009,-0.60000000000000009,"2018-06-28T18:30:09",-0.38000000000000006,-0.40269230769230774]
[6,28,2018,18,31,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T18:31:19",-0.46500000000000002,-0.43961538461538469]
[6,28,2018,18,31,49,-0.42000000000000004,-0.42000000000000004,"2018-06-28T18:31:49",-0.41,-0.44307692307692303]
[6,28,2018,18,32,39,-0.39,-0.39,"2018-06-28T18:32:39",-0.41000000000000009,-0.43153846153846154]
[6,28,2018,18,33,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T18:33:39",-0.41500000000000004,-0.43730769230769234]
[6,28,2018,18,34,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T18:34:29",-0.44500000000000001,-0.44423076923076904]
[6,28,2018,18,35,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T18:35:19",-0.34,-0.40384615384615391]
[6,28,2018,18,36,19,-0.33,-0.33,"2018-06-28T18:36:19",-0.32000000000000006,{"$f":"AVERAGE(G3640:G3665)","v":-0.37961538461538463}]
[6,28,2018,18,37,9,-0.18,-0.18,"2018-06-28T18:37:09",-0.25,-0.34615384615384615]
[6,28,2018,18,37,19,-0.12,-0.12,"2018-06-28T18:37:19",-0.215,-0.33461538461538459]
[6,28,2018,18,38,9,-0.27,-0.27,"2018-06-28T18:38:09",-0.21000000000000005,-0.29884615384615382]
[6,28,2018,18,38,59,-0.27,-0.27,"2018-06-28T18:38:59",-0.27500000000000002,-0.26653846153846161]
[6,28,2018,18,39,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T18:39:59",-0.33,-0.27346153846153848]
[6,28,2018,18,40,49,-0.18,-0.18,"2018-06-28T18:40:49",-0.21999999999999997,-0.25153846153846154]
[6,28,2018,18,41,49,-0.24,-0.24,"2018-06-28T18:41:49",-0.17,-0.2457692307692308]
[6,28,2018,18,42,39,-0.39,-0.39,"2018-06-28T18:42:39",-0.31,-0.25846153846153858]
[6,28,2018,18,43,29,-0.06,-0.06,"2018-06-28T18:43:29",-0.18000000000000005,-0.23192307692307693]
[6,28,2018,18,44,29,-0.06,-0.06,"2018-06-28T18:44:29",-6.9999999999999993E-2,-0.17423076923076913]
[6,28,2018,18,44,49,-0.03,-0.03,"2018-06-28T18:44:49",-0.06,-0.16153846153846152]
[6,28,2018,18,45,59,-0.51,-0.51,"2018-06-28T18:45:59",-0.38500000000000006,-0.20999999999999996]
[6,28,2018,18,46,59,-0.48,-0.48,"2018-06-28T18:46:59",-0.46,{"$f":"AVERAGE(G3704:G3729)","v":-0.24461538461538465}]
[6,28,2018,18,47,49,-0.51,-0.51,"2018-06-28T18:47:49",-0.47499999999999992,-0.30923076923076925]
[6,28,2018,18,47,59,-0.57000000000000006,-0.57000000000000006,"2018-06-28T18:47:59",-0.49000000000000005,-0.32769230769230773]
[6,28,2018,18,48,49,-0.54,-0.54,"2018-06-28T18:48:49",-0.58500000000000008,-0.42807692307692319]
[6,28,2018,18,49,39,-0.60000000000000009,-0.60000000000000009,"2018-06-28T18:49:39",-0.56000000000000016,-0.50884615384615384]
[6,28,2018,18,50,39,-0.54,-0.54,"2018-06-28T18:50:39",-0.52,-0.52730769230769237]
[6,28,2018,18,51,29,-0.39,-0.39,"2018-06-28T18:51:29",-0.43500000000000005,-0.51576923076923098]
[6,28,2018,18,52,19,-0.39,-0.39,"2018-06-28T18:52:19",-0.42,-0.5030769230769232]
[6,28,2018,18,53,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T18:53:19",-0.33,-0.44538461538461543]
[6,28,2018,18,54,9,-0.51,-0.51,"2018-06-28T18:54:09",-0.40500000000000003,-0.41769230769230781]
[6,28,2018,18,55,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T18:55:09",-0.33499999999999996,-0.37846153846153846]
[6,28,2018,18,55,59,-0.12,-0.12,"2018-06-28T18:55:59",-0.19499999999999998,-0.33692307692307694]
[6,28,2018,18,56,49,-0.09,-0.09,"2018-06-28T18:56:49",-0.16,-0.28961538461538466]
[6,28,2018,18,57,49,-0.18,-0.18,"2018-06-28T18:57:49",-0.125,-0.24461538461538462]
[6,28,2018,18,58,39,-0.06,-0.06,"2018-06-28T18:58:39",-0.13,-0.18115384615384611]
[6,28,2018,18,58,49,-0.06,-0.06,"2018-06-28T18:58:49",-0.11000000000000003,-0.1661538461538461]
[6,28,2018,18,59,59,-0.03,-0.03,"2018-06-28T18:59:59",-0.14499999999999999,-0.13615384615384613]
[6,28,2018,19,0,19,-0.12,-0.12,"2018-06-28T19:00:19",-0.115,-0.13153846153846155]
[6,28,2018,19,1,19,-0.12,-0.12,"2018-06-28T19:01:19",-6.9999999999999993E-2,-0.11076923076923076]
[6,28,2018,19,2,9,-0.12,-0.12,"2018-06-28T19:02:09",-9.4999999999999987E-2,-0.10384615384615385]
[6,28,2018,19,2,59,-0.09,-0.09,"2018-06-28T19:02:59",-0.13500000000000001,-0.10730769230769233]
[6,28,2018,19,3,59,-0.12,-0.12,"2018-06-28T19:03:59",-0.13,-0.10384615384615385]
[6,28,2018,19,4,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T19:04:49",-0.23,-0.13730769230769233]
[6,28,2018,19,5,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T19:05:49",-0.34,-0.19730769230769235]
[6,28,2018,19,6,39,-0.36,-0.36,"2018-06-28T19:06:39",-0.34499999999999997,-0.24576923076923071]
[6,28,2018,19,7,29,-0.24,-0.24,"2018-06-28T19:07:29",-0.27999999999999997,-0.27230769230769231]
[6,28,2018,19,8,29,-0.27,-0.27,"2018-06-28T19:08:29",-0.30000000000000004,-0.30923076923076931]
[6,28,2018,19,9,19,-0.15000000000000002,-0.15000000000000002,"2018-06-28T19:09:19",-0.22999999999999998,-0.29653846153846164]
[6,28,2018,19,9,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T19:09:29",-0.20999999999999996,-0.29076923076923084]
[6,28,2018,19,10,19,-0.06,-0.06,"2018-06-28T19:10:19",-0.14500000000000002,-0.25384615384615394]
[6,28,2018,19,11,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T19:11:09",-0.12500000000000003,-0.20999999999999996]
[6,28,2018,19,12,9,-0.09,-0.09,"2018-06-28T19:12:09",-0.14500000000000002,-0.1857692307692308]
[6,28,2018,19,12,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T19:12:59",-9.9999999999999992E-2,-0.14653846153846153]
[6,28,2018,19,14,9,-0.21000000000000002,-0.21000000000000002,"2018-06-28T19:14:09",-0.27,-0.16269230769230772]
[6,28,2018,19,14,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T19:14:39",-0.22500000000000001,-0.1776923076923077]
[6,28,2018,19,15,29,-0.42000000000000004,-0.42000000000000004,"2018-06-28T19:15:29",-0.34500000000000003,-0.21923076923076923]
[6,28,2018,19,16,29,-0.60000000000000009,-0.60000000000000009,"2018-06-28T19:16:29",-0.54,-0.31038461538461537]
[6,28,2018,19,17,19,-0.48,-0.48,"2018-06-28T19:17:19",-0.55500000000000005,-0.39576923076923082]
[6,28,2018,19,18,9,-0.57000000000000006,-0.57000000000000006,"2018-06-28T19:18:09",-0.55500000000000016,-0.45115384615384618]
[6,28,2018,19,19,9,-0.36,-0.36,"2018-06-28T19:19:09",-0.42,-0.49153846153846154]
[6,28,2018,19,19,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T19:19:59",-0.40000000000000008,-0.49846153846153857]
[6,28,2018,19,20,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T19:20:49",-0.20499999999999999,-0.42576923076923101]
[6,28,2018,19,20,59,-0.18,-0.18,"2018-06-28T19:20:59",-0.18499999999999997,-0.41076923076923089]
[6,28,2018,19,21,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T19:21:49",-0.20499999999999999,-0.34846153846153854]
[6,28,2018,19,22,49,-0.33,-0.33,"2018-06-28T19:22:49",-0.26,-0.27692307692307694]
[6,28,2018,19,23,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T19:23:39",-0.29000000000000004,-0.2607692307692307]
[6,28,2018,19,24,29,-0.33,-0.33,"2018-06-28T19:24:29",-0.30000000000000004,-0.24576923076923077]
[6,28,2018,19,25,29,-0.51,-0.51,"2018-06-28T19:25:29",-0.43500000000000005,-0.30692307692307691]
[6,28,2018,19,26,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T19:26:19",{"$f":"AVERAGE(G3960:G3965)","v":-0.48500000000000004},-0.35653846153846153]
[6,28,2018,19,27,19,-0.57000000000000006,-0.57000000000000006,"2018-06-28T19:27:19",-0.56999999999999995,-0.42461538461538456]
[6,28,2018,19,28,9,-0.63,-0.63,"2018-06-28T19:28:09",-0.625,-0.49384615384615393]
[6,28,2018,19,28,39,-0.57000000000000006,-0.57000000000000006,"2018-06-28T19:28:39",-0.625,-0.52730769230769248]
[6,28,2018,19,29,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T19:29:49",-0.56500000000000006,-0.568846153846154]
[6,28,2018,19,30,39,-0.33,-0.33,"2018-06-28T19:30:39",-0.41499999999999998,-0.55499999999999994]
[6,28,2018,19,31,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T19:31:29",-0.24,-0.48807692307692313]
[6,28,2018,19,31,39,-0.18,-0.18,"2018-06-28T19:31:39",-0.21499999999999997,-0.47307692307692312]
[6,28,2018,19,32,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T19:32:29",-0.22,-0.39461538461538476]
[6,28,2018,19,33,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T19:33:29",-0.25,-0.30923076923076925]
[6,28,2018,19,34,19,-0.24,-0.24,"2018-06-28T19:34:19",-0.21,-0.25269230769230777]
[6,28,2018,19,35,9,-0.24,-0.24,"2018-06-28T19:35:09",-0.22999999999999998,-0.22500000000000006]
[6,28,2018,19,36,9,-0.06,-0.06,"2018-06-28T19:36:09",-0.21000000000000005,-0.22499999999999998]
[6,28,2018,19,36,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T19:36:59",{"$f":"AVERAGE(G4024:G4029)","v":-0.13},-0.20538461538461533]
[6,28,2018,19,37,49,-0.36,-0.36,"2018-06-28T19:37:49",-0.24,-0.21000000000000008]
[6,28,2018,19,38,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T19:38:49",-0.38499999999999995,-0.2492307692307692]
[6,28,2018,19,39,39,-0.33,-0.33,"2018-06-28T19:39:39",-0.31500000000000006,-0.26423076923076921]
[6,28,2018,19,40,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T19:40:39",-0.42499999999999999,-0.32307692307692304]
[6,28,2018,19,41,29,-0.48,-0.48,"2018-06-28T19:41:29",-0.505,-0.38884615384615384]
[6,28,2018,19,42,19,-0.57000000000000006,-0.57000000000000006,"2018-06-28T19:42:19",-0.55000000000000016,-0.44423076923076926]
[6,28,2018,19,42,49,-0.39,-0.39,"2018-06-28T19:42:49",-0.54500000000000015,-0.45807692307692316]
[6,28,2018,19,43,9,-0.51,-0.51,"2018-06-28T19:43:09",-0.52,-0.46615384615384625]
[6,28,2018,19,44,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T19:44:09",-0.43999999999999995,-0.49038461538461536]
[6,28,2018,19,44,59,-0.66,-0.66,"2018-06-28T19:44:59",-0.54500000000000004,-0.51692307692307693]
[6,28,2018,19,45,49,-0.60000000000000009,-0.60000000000000009,"2018-06-28T19:45:49",-0.64,-0.53884615384615375]
[6,28,2018,19,46,49,-0.39,-0.39,"2018-06-28T19:46:49",-0.54000000000000015,-0.53192307692307694]
[6,28,2018,19,47,39,-0.33,-0.33,"2018-06-28T19:47:39",{"$f":"AVERAGE(G4088:G4093)","v":-0.32500000000000001},-0.49961538461538485]
[6,28,2018,19,48,29,-0.42000000000000004,-0.42000000000000004,"2018-06-28T19:48:29",-0.39500000000000002,-0.49384615384615399]
[6,28,2018,19,49,29,-0.30000000000000004,-0.30000000000000004,"2018-06-28T19:49:29",-0.32500000000000001,-0.43384615384615388]
[6,28,2018,19,50,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T19:50:19",-0.35000000000000003,-0.38423076923076926]
[6,28,2018,19,51,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T19:51:19",-0.4549999999999999,-0.37499999999999994]
[6,28,2018,19,52,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T19:52:09",-0.4549999999999999,-0.39576923076923076]
[6,28,2018,19,52,59,-0.54,-0.54,"2018-06-28T19:52:59",-0.49500000000000005,-0.42115384615384627]
[6,28,2018,19,53,9,-0.51,-0.51,"2018-06-28T19:53:09",-0.5099999999999999,-0.42807692307692313]
[6,28,2018,19,53,59,-0.48,-0.48,"2018-06-28T19:53:59",-0.5,-0.46269230769230774]
[6,28,2018,19,54,59,-0.39,-0.39,"2018-06-28T19:54:59",-0.50000000000000011,-0.48576923076923073]
[6,28,2018,19,55,49,-0.57000000000000006,-0.57000000000000006,"2018-06-28T19:55:49",-0.51500000000000012,-0.50192307692307692]
[6,28,2018,19,56,59,-0.51,-0.51,"2018-06-28T19:56:59",-0.52999999999999992,-0.51923076923076905]
[6,28,2018,19,57,29,-0.51,-0.51,"2018-06-28T19:57:29",-0.5099999999999999,-0.51576923076923076]
[6,28,2018,19,58,19,-0.48,-0.48,"2018-06-28T19:58:19",{"$f":"AVERAGE(G4152:G4157)","v":-0.49},-0.51346153846153864]
[6,28,2018,19,59,9,-0.54,-0.54,"2018-06-28T19:59:09",-0.52500000000000002,-0.51576923076923076]
[6,28,2018,20,0,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T20:00:09",-0.35499999999999998,-0.47884615384615387]
[6,28,2018,20,0,59,-0.27,-0.27,"2018-06-28T20:00:59",-0.255,-0.42230769230769233]
[6,28,2018,20,1,59,-0.42000000000000004,-0.42000000000000004,"2018-06-28T20:01:59",-0.28000000000000003,-0.37038461538461542]
[6,28,2018,20,2,49,-0.54,-0.54,"2018-06-28T20:02:49",-0.48,-0.37269230769230777]
[6,28,2018,20,3,39,-0.44999999999999996,-0.44999999999999996,"2018-06-28T20:03:39",-0.52500000000000002,-0.37038461538461542]
[6,28,2018,20,3,49,-0.33,-0.33,"2018-06-28T20:03:49",-0.49000000000000005,-0.36692307692307691]
[6,28,2018,20,4,39,-0.33,-0.33,"2018-06-28T20:04:39",-0.35499999999999998,-0.37846153846153846]
[6,28,2018,20,5,29,-0.36,-0.36,"2018-06-28T20:05:29",-0.33500000000000002,-0.39576923076923076]
[6,28,2018,20,6,29,-0.51,-0.51,"2018-06-28T20:06:29",-0.505,-0.44076923076923075]
[6,28,2018,20,7,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T20:07:19",-0.375,-0.40961538461538477]
[6,28,2018,20,8,19,-0.30000000000000004,-0.30000000000000004,{"$f":"DATE(C4217,A4217,B4217)+TIME(D4217,E4217,F4217)","v":"2018-06-28T20:08:19"},-0.28500000000000003,-0.37038461538461542]
[6,28,2018,20,9,9,-0.36,-0.36,"2018-06-28T20:09:09",-0.32500000000000001,-0.36461538461538456]
[6,28,2018,20,9,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T20:09:59",-0.32,-0.36]
[6,28,2018,20,10,59,-0.27,-0.27,"2018-06-28T20:10:59",-0.29000000000000004,-0.3034615384615385]
[6,28,2018,20,11,29,-0.36,-0.36,"2018-06-28T20:11:29",-0.30499999999999999,-0.30576923076923079]
[6,28,2018,20,12,39,-0.60000000000000009,-0.60000000000000009,"2018-06-28T20:12:39",-0.59000000000000008,-0.37961538461538458]
[6,28,2018,20,13,29,-0.54,-0.54,"2018-06-28T20:13:29",-0.5099999999999999,-0.41076923076923078]
[6,28,2018,20,14,19,-0.57000000000000006,-0.57000000000000006,"2018-06-28T20:14:19",-0.55000000000000016,-0.45692307692307688]
[6,28,2018,20,14,29,-0.60000000000000009,-0.60000000000000009,"2018-06-28T20:14:29",-0.56000000000000016,-0.46846153846153837]
[6,28,2018,20,15,19,-0.63,-0.63,"2018-06-28T20:15:19",-0.61499999999999999,-0.53192307692307694]
[6,28,2018,20,16,9,-0.60000000000000009,-0.60000000000000009,"2018-06-28T20:16:09",-0.62,-0.57576923076923092]
[6,28,2018,20,17,9,-0.57000000000000006,-0.57000000000000006,"2018-06-28T20:17:09",-0.58500000000000008,-0.57807692307692315]
[6,28,2018,20,17,59,-0.60000000000000009,-0.60000000000000009,"2018-06-28T20:17:59",-0.57000000000000006,-0.59076923076923082]
[6,28,2018,20,18,59,-0.54,-0.54,{"$f":"DATE(C4281,A4281,B4281)+TIME(D4281,E4281,F4281)","v":"2018-06-28T20:18:59"},-0.56500000000000006,-0.58961538461538454]
[6,28,2018,20,19,49,-0.66,-0.66,"2018-06-28T20:19:49",-0.55000000000000004,-0.57576923076923059]
[6,28,2018,20,20,39,-0.66,-0.66,"2018-06-28T20:20:39",-0.64,-0.57923076923076922]
[6,28,2018,20,21,39,-0.48,-0.48,"2018-06-28T20:21:39",-0.53,-0.56769230769230794]
[6,28,2018,20,22,29,-0.51,-0.51,"2018-06-28T20:22:29",-0.47499999999999992,-0.54923076923076919]
[6,28,2018,20,23,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T20:23:19",-0.43999999999999995,-0.52384615384615385]
[6,28,2018,20,24,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T20:24:19",-0.34500000000000003,-0.47307692307692312]
[6,28,2018,20,25,9,-0.24,-0.24,"2018-06-28T20:25:09",-0.28500000000000003,-0.40846153846153854]
[6,28,2018,20,25,39,-0.27,-0.27,"2018-06-28T20:25:39",-0.27,-0.37500000000000006]
[6,28,2018,20,25,59,-0.24,-0.24,"2018-06-28T20:25:59",-0.255,-0.35653846153846147]
[6,28,2018,20,26,49,-0.33,-0.33,"2018-06-28T20:26:49",-0.23,-0.30923076923076925]
[6,28,2018,20,27,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T20:27:49",-0.38999999999999996,-0.30230769230769239]
[6,28,2018,20,28,39,-0.36,-0.36,"2018-06-28T20:28:39",-0.39499999999999996,-0.3115384615384616]
[6,28,2018,20,29,39,-0.44999999999999996,-0.44999999999999996,{"$f":"DATE(C4345,A4345,B4345)+TIME(D4345,E4345,F4345)","v":"2018-06-28T20:29:39"},-0.43500000000000005,-0.34846153846153843]
[6,28,2018,20,30,29,-0.44999999999999996,-0.44999999999999996,"2018-06-28T20:30:29",-0.4200000000000001,-0.37961538461538463]
[6,28,2018,20,31,19,-0.36,-0.36,"2018-06-28T20:31:19",-0.38999999999999996,-0.40269230769230757]
[6,28,2018,20,32,19,-0.48,-0.48,"2018-06-28T20:32:19",-0.41499999999999998,-0.40499999999999992]
[6,28,2018,20,33,9,-0.54,-0.54,"2018-06-28T20:33:09",-0.49,-0.42807692307692319]
[6,28,2018,20,33,59,-0.48,-0.48,"2018-06-28T20:33:59",-0.53500000000000003,-0.4453846153846156]
[6,28,2018,20,34,59,-0.69000000000000006,-0.69000000000000006,"2018-06-28T20:34:59",-0.59,-0.48230769230769227]
[6,28,2018,20,35,49,-0.54,-0.54,"2018-06-28T20:35:49",-0.67500000000000016,-0.5446153846153845]
[6,28,2018,20,35,59,-0.51,-0.51,"2018-06-28T20:35:59",-0.64500000000000002,-0.54923076923076908]
[6,28,2018,20,36,49,-0.72,-0.72,"2018-06-28T20:36:49",-0.59,-0.5803846153846155]
[6,28,2018,20,37,39,-0.72,-0.72,"2018-06-28T20:37:39",-0.68500000000000005,-0.61615384615384616]
[6,28,2018,20,38,39,-0.51,-0.51,"2018-06-28T20:38:39",-0.52999999999999992,-0.61384615384615382]
[6,28,2018,20,39,49,-0.48,-0.48,"2018-06-28T20:39:49",-0.49,-0.56653846153846166]
[6,28,2018,20,40,19,-0.39,-0.39,{"$f":"DATE(C4409,A4409,B4409)+TIME(D4409,E4409,F4409)","v":"2018-06-28T20:40:19"},-0.46500000000000002,-0.55038461538461536]
[6,28,2018,20,41,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T20:41:09",-0.34999999999999992,-0.49961538461538463]
[6,28,2018,20,41,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T20:41:59",-0.27500000000000002,-0.42115384615384627]
[6,28,2018,20,42,59,-0.33,-0.33,"2018-06-28T20:42:59",-0.25,-0.35653846153846153]
[6,28,2018,20,43,49,-0.39,-0.39,"2018-06-28T20:43:49",-0.39000000000000007,-0.34038461538461529]
[6,28,2018,20,44,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T20:44:39",-0.37999999999999995,-0.32538461538461544]
[6,28,2018,20,45,39,-0.51,-0.51,"2018-06-28T20:45:39",-0.44500000000000001,-0.35076923076923083]
[6,28,2018,20,46,29,-0.57000000000000006,-0.57000000000000006,"2018-06-28T20:46:29",-0.54,-0.40730769230769232]
[6,28,2018,20,46,39,-0.57000000000000006,-0.57000000000000006,"2018-06-28T20:46:39",-0.55000000000000016,-0.42230769230769233]
[6,28,2018,20,47,29,-0.63,-0.63,"2018-06-28T20:47:29",-0.6,-0.48115384615384621]
[6,28,2018,20,48,19,-0.60000000000000009,-0.60000000000000009,"2018-06-28T20:48:19",-0.62,-0.52384615384615396]
[6,28,2018,20,49,19,-0.42000000000000004,-0.42000000000000004,"2018-06-28T20:49:19",-0.48,-0.54346153846153844]
[6,28,2018,20,50,9,-0.27,-0.27,"2018-06-28T20:50:09",-0.36000000000000004,-0.52038461538461533]
[6,28,2018,20,50,59,-0.15000000000000002,-0.15000000000000002,{"$f":"DATE(C4473,A4473,B4473)+TIME(D4473,E4473,F4473)","v":"2018-06-28T20:50:59"},-0.25499999999999995,-0.46153846153846156]
[6,28,2018,20,51,59,-0.03,-0.03,"2018-06-28T20:51:59",-9.5000000000000015E-2,-0.34269230769230768]
[6,28,2018,20,52,49,-0.06,-0.06,"2018-06-28T20:52:49",-0.02,-0.23076923076923081]
[6,28,2018,20,53,49,-0.03,-0.03,"2018-06-28T20:53:49",-0.06,-0.13961538461538459]
[6,28,2018,20,54,19,-0.03,-0.03,"2018-06-28T20:54:19",-4.5000000000000005E-2,-0.10153846153846148]
[6,28,2018,20,55,19,-0.24,-0.24,"2018-06-28T20:55:19",-0.16500000000000001,-8.0769230769230788E-2]
[6,28,2018,20,56,19,-0.24,-0.24,"2018-06-28T20:56:19",-0.22500000000000001,-0.11076923076923076]
[6,28,2018,20,57,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T20:57:09",-0.29000000000000004,-0.16499999999999998]
[6,28,2018,20,57,19,-0.33,-0.33,"2018-06-28T20:57:19",-0.30500000000000005,-0.17653846153846153]
[6,28,2018,20,58,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T20:58:09",-0.375,-0.23769230769230765]
[6,28,2018,20,58,59,-0.54,-0.54,"2018-06-28T20:58:59",-0.49000000000000005,-0.32423076923076921]
[6,28,2018,20,59,59,-0.54,-0.54,"2018-06-28T20:59:59",-0.56500000000000006,-0.40615384615384625]
[6,28,2018,21,0,49,-0.54,-0.54,"2018-06-28T21:00:49",-0.54500000000000004,-0.46499999999999997]
[6,28,2018,21,1,39,-0.54,-0.54,{"$f":"DATE(C4537,A4537,B4537)+TIME(D4537,E4537,F4537)","v":"2018-06-28T21:01:39"},-0.52500000000000002,-0.50653846153846149]
[6,28,2018,21,2,39,-0.51,-0.51,"2018-06-28T21:02:39",-0.55500000000000005,-0.54346153846153844]
[6,28,2018,21,3,29,-0.54,-0.54,"2018-06-28T21:03:29",-0.51,-0.53999999999999992]
[6,28,2018,21,4,29,-0.51,-0.51,"2018-06-28T21:04:29",-0.5099999999999999,-0.52846153846153843]
[6,28,2018,21,5,19,-0.51,-0.51,"2018-06-28T21:05:19",-0.48500000000000004,-0.51576923076923087]
[6,28,2018,21,6,9,-0.54,-0.54,"2018-06-28T21:06:09",-0.54500000000000004,-0.52153846153846151]
[6,28,2018,21,7,9,-0.54,-0.54,"2018-06-28T21:07:09",-0.56000000000000005,-0.52499999999999991]
[6,28,2018,21,7,59,-0.75,-0.75,"2018-06-28T21:07:59",-0.625,-0.5492307692307693]
[6,28,2018,21,8,29,-0.75,-0.75,"2018-06-28T21:08:29",-0.72000000000000008,-0.57692307692307687]
[6,28,2018,21,8,49,-0.72,-0.72,"2018-06-28T21:08:49",-0.745,-0.59423076923076934]
[6,28,2018,21,9,39,-0.84000000000000008,-0.84000000000000008,"2018-06-28T21:09:39",-0.79,-0.65653846153846152]
[6,28,2018,21,10,39,-0.57000000000000006,-0.57000000000000006,"2018-06-28T21:10:39",-0.58000000000000007,-0.66230769230769226]
[6,28,2018,21,11,29,-0.51,-0.51,"2018-06-28T21:11:29",-0.52499999999999991,-0.65423076923076939]
[6,28,2018,21,12,19,-0.48,-0.48,{"$f":"DATE(C4601,A4601,B4601)+TIME(D4601,E4601,F4601)","v":"2018-06-28T21:12:19"},-0.48,-0.62192307692307702]
[6,28,2018,21,13,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T21:13:19",-0.35499999999999998,-0.53076923076923088]
[6,28,2018,21,14,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T21:14:09",-0.31500000000000006,-0.44423076923076937]
[6,28,2018,21,15,9,-0.48,-0.48,"2018-06-28T21:15:09",-0.35499999999999998,-0.39461538461538459]
[6,28,2018,21,15,59,-0.36,-0.36,"2018-06-28T21:15:59",-0.42,-0.37730769230769223]
[6,28,2018,21,16,49,-0.18,-0.18,"2018-06-28T21:16:49",-0.31,-0.34384615384615391]
[6,28,2018,21,17,49,-0.33,-0.33,"2018-06-28T21:17:49",-0.21,-0.31499999999999989]
[6,28,2018,21,18,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T21:18:39",-0.27500000000000002,-0.30692307692307685]
[6,28,2018,21,19,29,-0.27,-0.27,"2018-06-28T21:19:29",-0.21,-0.27230769230769231]
[6,28,2018,21,19,39,-0.27,-0.27,"2018-06-28T21:19:39",-0.20499999999999999,-0.26538461538461539]
[6,28,2018,21,20,29,-0.42000000000000004,-0.42000000000000004,"2018-06-28T21:20:29",-0.42499999999999999,-0.27923076923076917]
[6,28,2018,21,21,29,-0.42000000000000004,-0.42000000000000004,"2018-06-28T21:21:29",-0.41,-0.31500000000000006]
[6,28,2018,21,22,19,-0.51,-0.51,"2018-06-28T21:22:19",-0.46500000000000002,-0.3611538461538461]
[6,28,2018,21,22,59,-0.42000000000000004,-0.42000000000000004,{"$f":"DATE(C4665,A4665,B4665)+TIME(D4665,E4665,F4665)","v":"2018-06-28T21:22:59"},-0.49,-0.39461538461538459]
[6,28,2018,21,23,59,-0.44999999999999996,-0.44999999999999996,"2018-06-28T21:23:59",-0.43999999999999995,-0.44884615384615373]
[6,28,2018,21,24,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T21:24:49",-0.4549999999999999,-0.44884615384615373]
[6,28,2018,21,25,49,-0.48,-0.48,"2018-06-28T21:25:49",-0.46499999999999991,-0.46153846153846156]
[6,28,2018,21,26,39,-0.57000000000000006,-0.57000000000000006,"2018-06-28T21:26:39",-0.51500000000000001,-0.47076923076923083]
[6,28,2018,21,27,29,-0.54,-0.54,"2018-06-28T21:27:29",-0.58000000000000007,-0.49153846153846159]
[6,28,2018,21,28,29,-0.57000000000000006,-0.57000000000000006,"2018-06-28T21:28:29",-0.55500000000000016,-0.51807692307692299]
[6,28,2018,21,29,19,-0.54,-0.54,"2018-06-28T21:29:19",-0.55500000000000005,-0.53653846153846141]
[6,28,2018,21,30,9,-0.39,-0.39,"2018-06-28T21:30:09",-0.47500000000000003,-0.53538461538461535]
[6,28,2018,21,30,19,-0.33,-0.33,"2018-06-28T21:30:19",-0.44,-0.5296153846153846]
[6,28,2018,21,31,9,-0.54,-0.54,"2018-06-28T21:31:09",-0.44500000000000001,-0.51461538461538459]
[6,28,2018,21,32,9,-0.36,-0.36,"2018-06-28T21:32:09",-0.45500000000000002,-0.48807692307692285]
[6,28,2018,21,32,59,-0.39,-0.39,"2018-06-28T21:32:59",-0.36999999999999994,-0.45230769230769224]
[6,28,2018,21,33,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T21:33:49",-0.42499999999999999,-0.43153846153846154]
[6,28,2018,21,34,49,-0.36,-0.36,"2018-06-28T21:34:49",-0.38500000000000001,-0.42461538461538456]
[6,28,2018,21,35,39,-0.33,-0.33,"2018-06-28T21:35:39",-0.35499999999999998,-0.3957692307692306]
[6,28,2018,21,36,29,-0.36,-0.36,"2018-06-28T21:36:29",-0.35000000000000003,-0.37961538461538458]
[6,28,2018,21,37,9,-0.27,-0.27,"2018-06-28T21:37:09",-0.32,-0.36807692307692325]
[6,28,2018,21,38,9,-0.30000000000000004,-0.30000000000000004,"2018-06-28T21:38:09",-0.27,-0.33230769230769225]
[6,28,2018,21,39,9,-0.33,-0.33,"2018-06-28T21:39:09",-0.32000000000000006,-0.31730769230769218]
[6,28,2018,21,39,59,-0.36,-0.36,"2018-06-28T21:39:59",-0.33500000000000002,-0.31384615384615383]
[6,28,2018,21,40,49,-0.51,-0.51,"2018-06-28T21:40:49",-0.36500000000000005,-0.31615384615384617]
[6,28,2018,21,40,59,-0.51,-0.51,"2018-06-28T21:40:59",-0.38999999999999996,-0.32423076923076927]
[6,28,2018,21,41,49,-0.54,-0.54,"2018-06-28T21:41:49",-0.58500000000000008,-0.38538461538461549]
[6,28,2018,21,42,49,-0.63,-0.63,"2018-06-28T21:42:49",-0.57999999999999996,-0.45346153846153847]
[6,28,2018,21,43,39,-0.63,-0.63,"2018-06-28T21:43:39",-0.63,-0.51230769230769246]
[6,28,2018,21,44,29,-0.66,-0.66,"2018-06-28T21:44:29",-0.69499999999999995,-0.58384615384615401]
[6,28,2018,21,45,29,-0.48,-0.48,"2018-06-28T21:45:29",-0.52500000000000002,-0.60576923076923084]
[6,28,2018,21,46,19,-0.36,-0.36,"2018-06-28T21:46:19",-0.42,-0.57000000000000006]
[6,28,2018,21,47,9,-0.24,-0.24,"2018-06-28T21:47:09",-0.32500000000000001,-0.51807692307692299]
[6,28,2018,21,48,9,-0.15000000000000002,-0.15000000000000002,"2018-06-28T21:48:09",-0.17,-0.40730769230769237]
[6,28,2018,21,48,59,-0.12,-0.12,"2018-06-28T21:48:59",-0.13,-0.30000000000000004]
[6,28,2018,21,49,59,-0.09,-0.09,"2018-06-28T21:49:59",-9.9999999999999992E-2,-0.20884615384615388]
[6,28,2018,21,50,49,-0.12,-0.12,"2018-06-28T21:50:49",-0.11,-0.15576923076923077]
[6,28,2018,21,51,19,-0.27,-0.27,"2018-06-28T21:51:19",-0.16500000000000001,-0.14192307692307693]
[6,28,2018,21,51,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T21:51:39",-0.22,-0.14653846153846156]
[6,28,2018,21,52,29,-0.33,-0.33,"2018-06-28T21:52:29",-0.31000000000000005,-0.17538461538461542]
[6,28,2018,21,53,29,-0.36,-0.36,"2018-06-28T21:53:29",-0.35499999999999993,-0.22846153846153852]
[6,28,2018,21,54,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T21:54:19",-0.375,-0.2826923076923078]
[6,28,2018,21,55,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T21:55:09",-0.44500000000000001,-0.3461538461538462]
[6,28,2018,21,56,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T21:56:09",-0.435,-0.38884615384615384]
[6,28,2018,21,56,59,-0.33,-0.33,"2018-06-28T21:56:59",-0.36999999999999994,-0.39692307692307688]
[6,28,2018,21,57,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T21:57:49",-0.27500000000000002,-0.37846153846153857]
[6,28,2018,21,58,49,-0.15000000000000002,-0.15000000000000002,"2018-06-28T21:58:49",-0.17,-0.32769230769230773]
[6,28,2018,21,59,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T21:59:39",-0.14000000000000001,-0.2688461538461539]
[6,28,2018,22,0,39,0.03,0.03,"2018-06-28T22:00:39",-0.04,-0.18115384615384619]
[6,28,2018,22,1,29,0,0,"2018-06-28T22:01:29",0.04,-0.10615384615384614]
[6,28,2018,22,2,19,0.09,0.09,"2018-06-28T22:02:19",2.4999999999999998E-2,-5.4230769230769228E-2]
[6,28,2018,22,2,29,-0.03,-0.03,"2018-06-28T22:02:29",0.02,-4.9615384615384603E-2]
[6,28,2018,22,3,19,0,0,"2018-06-28T22:03:19",-1.4999999999999999E-2,-1.9615384615384611E-2]
[6,28,2018,22,4,9,-0.06,-0.06,"2018-06-28T22:04:09",-0.03,0]
[6,28,2018,22,5,9,-0.12,-0.12,"2018-06-28T22:05:09",-8.9999999999999983E-2,-1.9615384615384611E-2]
[6,28,2018,22,5,49,-0.18,-0.18,"2018-06-28T22:05:49",-0.16,-5.4230769230769221E-2]
[6,28,2018,22,6,49,-0.57000000000000006,-0.57000000000000006,"2018-06-28T22:06:49",-0.32500000000000001,-0.13384615384615386]
[6,28,2018,22,7,39,-0.63,-0.63,"2018-06-28T22:07:39",-0.6,-0.24807692307692306]
[6,28,2018,22,8,29,-0.54,-0.54,"2018-06-28T22:08:29",-0.5099999999999999,-0.33461538461538459]
[6,28,2018,22,9,29,-0.57000000000000006,-0.57000000000000006,"2018-06-28T22:09:29",-0.55500000000000005,-0.44192307692307692]
[6,28,2018,22,10,19,-0.60000000000000009,-0.60000000000000009,"2018-06-28T22:10:19",-0.58000000000000007,-0.51692307692307693]
[6,28,2018,22,11,19,-0.63,-0.63,"2018-06-28T22:11:19",-0.64,-0.57576923076923092]
[6,28,2018,22,12,9,-0.89999999999999991,-0.89999999999999991,"2018-06-28T22:12:09",-0.77500000000000002,-0.61730769230769234]
[6,28,2018,22,12,59,-0.69000000000000006,-0.69000000000000006,"2018-06-28T22:12:59",-0.82000000000000017,-0.67730769230769228]
[6,28,2018,22,13,9,-0.66,-0.66,"2018-06-28T22:13:09",-0.77999999999999992,-0.68307692307692303]
[6,28,2018,22,13,59,-0.51,-0.51,"2018-06-28T22:13:59",-0.58500000000000008,-0.68192307692307697]
[6,28,2018,22,14,49,-0.33,-0.33,"2018-06-28T22:14:49",-0.42,-0.6449999999999998]
[6,28,2018,22,15,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T22:15:49",-0.245,-0.55153846153846153]
[6,28,2018,22,16,39,-0.24,-0.24,"2018-06-28T22:16:39",-0.215,-0.43038461538461559]
[6,28,2018,22,17,39,-0.30000000000000004,-0.30000000000000004,"2018-06-28T22:17:39",-0.30500000000000005,-0.33230769230769241]
[6,28,2018,22,18,29,-0.36,-0.36,"2018-06-28T22:18:29",-0.31000000000000005,-0.28846153846153844]
[6,28,2018,22,19,19,-0.36,-0.36,"2018-06-28T22:19:19",-0.33499999999999996,-0.28038461538461534]
[6,28,2018,22,19,59,-0.33,-0.33,"2018-06-28T22:19:59",-0.37000000000000005,-0.30115384615384616]
[6,28,2018,22,20,59,-0.51,-0.51,"2018-06-28T22:20:59",-0.40499999999999997,-0.34500000000000003]
[6,28,2018,22,21,49,-0.57000000000000006,-0.57000000000000006,"2018-06-28T22:21:49",-0.53500000000000014,-0.39]
[6,28,2018,22,22,49,-0.36,-0.36,"2018-06-28T22:22:49",-0.55000000000000004,-0.44538461538461538]
[6,28,2018,22,23,39,-0.48,-0.48,"2018-06-28T22:23:39",-0.435,-0.46846153846153843]
[6,28,2018,22,23,49,-0.48,-0.48,"2018-06-28T22:23:49",-0.45500000000000002,-0.47076923076923077]
[6,28,2018,22,24,39,-0.42000000000000004,-0.42000000000000004,"2018-06-28T22:24:39",-0.44500000000000001,-0.48692307692307701]
[6,28,2018,22,25,29,-0.39,-0.39,"2018-06-28T22:25:29",-0.38500000000000001,-0.47423076923076929]
[6,28,2018,22,26,29,-0.54,-0.54,"2018-06-28T22:26:29",-0.48500000000000004,-0.45461538461538464]
[6,28,2018,22,27,19,-0.60000000000000009,-0.60000000000000009,"2018-06-28T22:27:19",-0.57000000000000006,-0.46846153846153832]
[6,28,2018,22,28,19,-0.51,-0.51,"2018-06-28T22:28:19",-0.56999999999999995,-0.4926923076923076]
[6,28,2018,22,29,9,-0.36,-0.36,"2018-06-28T22:29:09",-0.44,-0.49384615384615377]
[6,28,2018,22,29,59,-0.48,-0.48,"2018-06-28T22:29:59",-0.38500000000000001,-0.49615384615384611]
[6,28,2018,22,30,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T22:30:59",-0.43499999999999989,{"$f":"AVERAGE(G5048:G5073)","v":-0.47653846153846163}]
[6,28,2018,22,31,49,-0.24,-0.24,"2018-06-28T22:31:49",-0.27,-0.41653846153846152]
[6,28,2018,22,32,39,-0.33,-0.33,"2018-06-28T22:32:39",-0.29000000000000004,-0.36576923076923074]
[6,28,2018,22,33,39,-0.33,-0.33,"2018-06-28T22:33:39",-0.33500000000000002,-0.34846153846153843]
[6,28,2018,22,34,29,-0.33,-0.33,"2018-06-28T22:34:29",-0.33,-0.33115384615384619]
[6,28,2018,22,35,9,-0.48,-0.48,"2018-06-28T22:35:09",-0.39999999999999997,-0.32769230769230767]
[6,28,2018,22,35,19,-0.51,-0.51,"2018-06-28T22:35:19",-0.43,-0.33576923076923076]
[6,28,2018,22,36,9,-0.54,-0.54,"2018-06-28T22:36:09",-0.49499999999999994,-0.37961538461538463]
[6,28,2018,22,37,9,-0.24,-0.24,"2018-06-28T22:37:09",-0.36500000000000005,-0.39230769230769236]
[6,28,2018,22,37,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T22:37:59",-0.25,-0.37730769230769223]
[6,28,2018,22,38,59,-0.12,-0.12,"2018-06-28T22:38:59",-0.16,-0.338076923076923]
[6,28,2018,22,39,49,-0.33,-0.33,"2018-06-28T22:39:49",-0.17,-0.27923076923076917]
[6,28,2018,22,40,39,-0.33,-0.33,"2018-06-28T22:40:39",-0.30000000000000004,-0.24115384615384611]
[6,28,2018,22,41,39,-0.15000000000000002,-0.15000000000000002,"2018-06-28T22:41:39",-0.16500000000000001,{"$f":"AVERAGE(G5112:G5137)","v":-0.20423076923076924}]
[6,28,2018,22,42,29,-0.15000000000000002,-0.15000000000000002,"2018-06-28T22:42:29",-0.14000000000000001,-0.1857692307692308]
[6,28,2018,22,43,19,-0.18,-0.18,"2018-06-28T22:43:19",-0.16000000000000003,-0.18692307692307697]
[6,28,2018,22,44,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T22:44:19",-0.215,-0.19153846153846155]
[6,28,2018,22,45,9,-0.27,-0.27,"2018-06-28T22:45:09",-0.26,-0.18923076923076923]
[6,28,2018,22,45,19,-0.27,-0.27,"2018-06-28T22:45:19",-0.27,-0.19384615384615381]
[6,28,2018,22,46,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T22:46:09",-0.36500000000000005,-0.23653846153846159]
[6,28,2018,22,46,59,-0.57000000000000006,-0.57000000000000006,"2018-06-28T22:46:59",-0.52500000000000002,-0.31615384615384612]
[6,28,2018,22,47,59,-0.24,-0.24,"2018-06-28T22:47:59",-0.41,-0.36807692307692308]
[6,28,2018,22,48,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T22:48:39",-0.20999999999999996,-0.36461538461538462]
[6,28,2018,22,49,29,-0.33,-0.33,"2018-06-28T22:49:29",-0.33,-0.3807692307692308]
[6,28,2018,22,50,29,-0.27,-0.27,"2018-06-28T22:50:29",-0.28500000000000003,-0.36230769230769239]
[6,28,2018,22,51,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T22:51:19",-0.28500000000000003,-0.31384615384615377]
[6,28,2018,22,52,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T22:52:19",-0.64,{"$f":"AVERAGE(G5176:G5201)","v":-0.36692307692307696}]
[6,28,2018,22,53,9,-0.39,-0.39,"2018-06-28T22:53:09",-0.35500000000000004,-0.39230769230769241]
[6,28,2018,22,53,59,-0.60000000000000009,-0.60000000000000009,"2018-06-28T22:53:59",-0.51,-0.43038461538461542]
[6,28,2018,22,54,59,-0.81,-0.81,"2018-06-28T22:54:59",-0.82,-0.55499999999999994]
[6,28,2018,22,55,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T22:55:49",-0.57500000000000007,-0.58846153846153837]
[6,28,2018,22,55,59,-0.39,-0.39,"2018-06-28T22:55:59",-0.505,-0.5446153846153845]
[6,28,2018,22,56,49,-0.51,-0.51,"2018-06-28T22:56:49",-0.42499999999999999,-0.54923076923076919]
[6,28,2018,22,57,39,-1.2000000000000002,-1.2000000000000002,"2018-06-28T22:57:39",-1.01,-0.6876923076923076]
[6,28,2018,22,58,39,-0.51,-0.51,"2018-06-28T22:58:39",-0.56499999999999995,-0.67730769230769217]
[6,28,2018,22,59,29,-0.18,-0.18,"2018-06-28T22:59:29",-0.27499999999999997,-0.55730769230769228]
[6,28,2018,23,0,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T23:00:19",-0.19999999999999998,-0.51]
[6,28,2018,23,1,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T23:01:19",-0.33499999999999996,-0.48346153846153855]
[6,28,2018,23,2,9,-0.44999999999999996,-0.44999999999999996,"2018-06-28T23:02:09",-0.46500000000000002,-0.35653846153846153]
[6,28,2018,23,2,49,-0.57000000000000006,-0.57000000000000006,"2018-06-28T23:02:49",-0.44000000000000011,-0.33807692307692311]
[6,28,2018,23,3,49,-0.78,-0.78,"2018-06-28T23:03:49",-0.62000000000000011,-0.4176923076923077]
[6,28,2018,23,4,39,-0.69000000000000006,-0.69000000000000006,"2018-06-28T23:04:39",-0.68500000000000005,-0.50653846153846149]
[6,28,2018,23,5,39,-0.33,-0.33,"2018-06-28T23:05:39",-0.44500000000000001,-0.53192307692307683]
[6,28,2018,23,6,29,-0.24,-0.24,"2018-06-28T23:06:29",-0.29499999999999998,-0.49730769230769245]
[6,28,2018,23,6,39,-0.21000000000000002,-0.21000000000000002,"2018-06-28T23:06:39",-0.27500000000000002,-0.4892307692307693]
[6,28,2018,23,7,29,-0.18,-0.18,"2018-06-28T23:07:29",-0.19000000000000003,-0.42923076923076942]
[6,28,2018,23,8,19,-0.09,-0.09,"2018-06-28T23:08:19",-0.15,-0.33461538461538465]
[6,28,2018,23,9,19,0,0,"2018-06-28T23:09:19",0.02,-0.1846153846153846]
[6,28,2018,23,10,9,-0.27,-0.27,"2018-06-28T23:10:09",-0.14499999999999999,-0.14307692307692307]
[6,28,2018,23,10,59,-0.51,-0.51,"2018-06-28T23:10:59",-0.37000000000000005,-0.1673076923076923]
[6,28,2018,23,11,59,-0.48,-0.48,"2018-06-28T23:11:59",-0.46,-0.22961538461538464]
[6,28,2018,23,12,49,-0.30000000000000004,-0.30000000000000004,"2018-06-28T23:12:49",-0.43999999999999995,-0.29192307692307695]
[6,28,2018,23,13,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T23:13:49",-0.375,-0.3830769230769232]
[6,28,2018,23,14,39,-0.51,-0.51,"2018-06-28T23:14:39",-0.46500000000000002,-0.42923076923076919]
[6,28,2018,23,15,29,-0.57000000000000006,-0.57000000000000006,"2018-06-28T23:15:29",-0.56000000000000005,-0.45807692307692316]
[6,28,2018,23,16,29,-0.48,-0.48,"2018-06-28T23:16:29",-0.5,-0.46730769230769237]
[6,28,2018,23,17,19,-0.36,-0.36,"2018-06-28T23:17:19",-0.435,-0.47307692307692317]
[6,28,2018,23,17,59,-0.36,-0.36,"2018-06-28T23:17:59",-0.35000000000000003,-0.46730769230769237]
[6,28,2018,23,18,9,-0.36,-0.36,"2018-06-28T23:18:09",-0.34999999999999992,-0.46384615384615391]
[6,28,2018,23,18,59,-0.09,-0.09,"2018-06-28T23:18:59",-0.255,-0.41884615384615392]
[6,28,2018,23,19,59,-0.15000000000000002,-0.15000000000000002,"2018-06-28T23:19:59",-0.13,-0.31846153846153852]
[6,28,2018,23,20,49,-0.33,-0.33,"2018-06-28T23:20:49",-0.18000000000000002,-0.25961538461538464]
[6,28,2018,23,21,39,-0.54,-0.54,"2018-06-28T23:21:39",-0.40500000000000003,-0.25846153846153852]
[6,28,2018,23,22,39,-0.66,-0.66,"2018-06-28T23:22:39",-0.64000000000000012,-0.32653846153846156]
[6,28,2018,23,23,29,-0.66,-0.66,"2018-06-28T23:23:29",-0.64500000000000002,-0.411923076923077]
[6,28,2018,23,24,29,-0.72,-0.72,"2018-06-28T23:24:29",-0.68499999999999994,-0.53884615384615409]
[6,28,2018,23,25,19,-0.51,-0.51,"2018-06-28T23:25:19",-0.56999999999999995,-0.60115384615384626]
[6,28,2018,23,26,9,-0.57000000000000006,-0.57000000000000006,"2018-06-28T23:26:09",-0.52,-0.61153846153846148]
[6,28,2018,23,27,9,-0.42000000000000004,-0.42000000000000004,"2018-06-28T23:27:09",-0.47,-0.56884615384615378]
[6,28,2018,23,27,59,-0.27,-0.27,"2018-06-28T23:27:59",-0.375,-0.51692307692307682]
[6,28,2018,23,28,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T23:28:49",-0.24,-0.42807692307692313]
[6,28,2018,23,28,59,-0.21000000000000002,-0.21000000000000002,"2018-06-28T23:28:59",-0.22999999999999998,-0.40961538461538471]
[6,28,2018,23,29,49,-0.21000000000000002,-0.21000000000000002,"2018-06-28T23:29:49",-0.24,-0.36000000000000004]
[6,28,2018,23,30,49,-0.44999999999999996,-0.44999999999999996,"2018-06-28T23:30:49",-0.26,-0.3]
[6,28,2018,23,31,29,-0.54,-0.54,"2018-06-28T23:31:29",-0.45500000000000002,-0.30807692307692314]
[6,28,2018,23,32,19,-0.33,-0.33,"2018-06-28T23:32:19",-0.38500000000000001,-0.30576923076923079]
[6,28,2018,23,33,19,-0.44999999999999996,-0.44999999999999996,"2018-06-28T23:33:19",-0.38999999999999996,-0.34269230769230763]
[6,28,2018,23,34,9,-0.36,-0.36,"2018-06-28T23:34:09",-0.42499999999999999,-0.37615384615384606]
[6,28,2018,23,34,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T23:34:59",-0.31,{"$f":"AVERAGE(G5432:G5457)","v":-0.39115384615384613}]
[6,28,2018,23,35,59,-0.03,-0.03,"2018-06-28T23:35:59",-0.19500000000000003,-0.32192307692307698]
[6,28,2018,23,36,49,0.03,0.03,"2018-06-28T23:36:49",1.4999999999999999E-2,-0.25615384615384612]
[6,28,2018,23,37,49,0.06,0.06,"2018-06-28T23:37:49",3.4999999999999996E-2,-0.15230769230769228]
[6,28,2018,23,38,39,0.06,0.06,"2018-06-28T23:38:39",4.9999999999999996E-2,-6.807692307692309E-2]
[6,28,2018,23,39,29,-0.06,-0.06,"2018-06-28T23:39:29",-5.5E-2,-2.6538461538461528E-2]
[6,28,2018,23,39,39,-0.06,-0.06,"2018-06-28T23:39:39",-7.4999999999999997E-2,-1.846153846153846E-2]
[6,28,2018,23,40,29,0.12,0.12,"2018-06-28T23:40:29",6.9999999999999993E-2,2.3076923076923075E-2]
[6,28,2018,23,41,29,-0.06,-0.06,"2018-06-28T23:41:29",-0.03,8.076923076923077E-3]
[6,28,2018,23,42,19,-0.21000000000000002,-0.21000000000000002,"2018-06-28T23:42:19",{"$f":"AVERAGE(G5496:G5501)","v":-0.10000000000000002},-1.9615384615384614E-2]
[6,28,2018,23,43,9,-0.48,-0.48,"2018-06-28T23:43:09",-0.33,-9.2307692307692299E-2]
[6,28,2018,23,44,9,-0.63,-0.63,"2018-06-28T23:44:09",-0.57999999999999996,-0.21346153846153845]
[6,28,2018,23,44,59,-0.63,-0.63,"2018-06-28T23:44:59",-0.63,-0.35538461538461541]
[6,28,2018,23,45,49,-0.84000000000000008,-0.84000000000000008,"2018-06-28T23:45:49",-0.69,-0.47884615384615398]
[6,28,2018,23,46,39,-0.86999999999999988,-0.86999999999999988,"2018-06-28T23:46:39",-0.84,-0.61961538461538468]
[6,28,2018,23,47,29,-0.51,-0.51,"2018-06-28T23:47:29",-0.6150000000000001,-0.66000000000000014]
[6,28,2018,23,48,29,-0.21000000000000002,-0.21000000000000002,"2018-06-28T23:48:29",-0.34500000000000003,-0.60576923076923084]
[6,28,2018,23,49,19,-0.24,-0.24,"2018-06-28T23:49:19",-0.22,-0.52730769230769237]
[6,28,2018,23,50,9,-0.12,-0.12,"2018-06-28T23:50:09",-0.17500000000000002,-0.4234615384615385]
[6,28,2018,23,50,19,-0.06,-0.06,"2018-06-28T23:50:19",-0.14500000000000002,-0.39346153846153864]
[6,28,2018,23,51,9,-0.18,-0.18,"2018-06-28T23:51:09",-0.12,-0.26538461538461539]
[6,28,2018,23,52,9,-0.18,-0.18,"2018-06-28T23:52:09",-0.17500000000000002,-0.18346153846153848]
[6,28,2018,23,52,59,-0.30000000000000004,-0.30000000000000004,"2018-06-28T23:52:59",{"$f":"AVERAGE(G5560:G5565)","v":-0.25},-0.1857692307692308]
[6,28,2018,23,53,49,-0.57000000000000006,-0.57000000000000006,"2018-06-28T23:53:49",-0.36000000000000004,-0.21346153846153848]
[6,28,2018,23,54,49,-0.51,-0.51,"2018-06-28T23:54:49",-0.59500000000000008,-0.32192307692307687]
[6,28,2018,23,55,39,-0.51,-0.51,"2018-06-28T23:55:39",-0.52,-0.39346153846153842]
[6,28,2018,23,56,29,-0.66,-0.66,"2018-06-28T23:56:29",-0.65,-0.49038461538461536]
[6,28,2018,23,57,29,-0.42000000000000004,-0.42000000000000004,"2018-06-28T23:57:29",-0.46,-0.53307692307692323]
[6,28,2018,23,58,19,-0.30000000000000004,-0.30000000000000004,"2018-06-28T23:58:19",-0.34500000000000003,-0.5146153846153847]
[6,28,2018,23,59,19,-0.12,-0.12,"2018-06-28T23:59:19",-0.21999999999999997,-0.43153846153846143]
[6,29,2018,0,0,9,-0.21000000000000002,-0.21000000000000002,"2018-06-29T00:00:09",-0.16,-0.35884615384615376]
[6,29,2018,0,0,49,-0.27,-0.27,"2018-06-29T00:00:49",-0.20499999999999999,-0.28499999999999992]
[6,29,2018,0,0,59,-0.27,-0.27,"2018-06-29T00:00:59",-0.22,-0.27115384615384602]
[6,29,2018,0,1,49,-0.18,-0.18,"2018-06-29T00:01:49",-0.24,-0.23423076923076919]
[6,29,2018,0,2,39,-0.09,-0.09,"2018-06-29T00:02:39",-0.10999999999999999,-0.1892307692307692]
[6,29,2018,0,3,39,-0.27,-0.27,"2018-06-29T00:03:39",{"$f":"AVERAGE(G5624:G5629)","v":-0.255},-0.19730769230769227]
[6,29,2018,0,4,29,-0.06,-0.06,"2018-06-29T00:04:29",-0.13500000000000001,-0.18576923076923074]
[6,29,2018,0,5,29,-0.12,-0.12,"2018-06-29T00:05:29",-4.5000000000000005E-2,-0.14423076923076922]
[6,29,2018,0,6,19,-0.27,-0.27,"2018-06-29T00:06:19",-0.17500000000000002,-0.13961538461538464]
[6,29,2018,0,7,9,-0.30000000000000004,-0.30000000000000004,"2018-06-29T00:07:09",-0.30000000000000004,-0.17653846153846156]
[6,29,2018,0,8,9,-0.48,-0.48,"2018-06-29T00:08:09",-0.42499999999999999,-0.2192307692307692]
[6,29,2018,0,8,59,-0.30000000000000004,-0.30000000000000004,"2018-06-29T00:08:59",-0.45500000000000007,-0.28730769230769232]
[6,29,2018,0,9,59,-0.18,-0.18,"2018-06-29T00:09:59",-0.23499999999999999,-0.32884615384615379]
[6,29,2018,0,10,49,-0.18,-0.18,"2018-06-29T00:10:49",-0.14499999999999999,-0.31269230769230766]
[6,29,2018,0,11,39,-0.06,-0.06,"2018-06-29T00:11:39",-0.125,-0.27461538461538454]
[6,29,2018,0,11,49,-0.06,-0.06,"2018-06-29T00:11:49",-0.10500000000000002,-0.26307692307692299]
[6,29,2018,0,12,39,-0.06,-0.06,"2018-06-29T00:12:39",-0.04,-0.18]
[6,29,2018,0,13,29,-0.06,-0.06,"2018-06-29T00:13:29",-0.06,-0.11192307692307693]
[6,29,2018,0,14,19,-0.06,-0.06,"2018-06-29T00:14:19",{"$f":"AVERAGE(G5688:G5693)","v":-4.5000000000000005E-2},-7.7307692307692327E-2]
[6,29,2018,0,15,9,-0.30000000000000004,-0.30000000000000004,"2018-06-29T00:15:09",-0.18000000000000002,-9.0000000000000024E-2]
[6,29,2018,0,16,9,-0.39,-0.39,"2018-06-29T00:16:09",-0.35500000000000004,-0.14769230769230773]
[6,29,2018,0,16,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T00:16:59",-0.4200000000000001,-0.22269230769230772]
[6,29,2018,0,17,49,-0.51,-0.51,"2018-06-29T00:17:49",-0.51500000000000001,-0.31269230769230771]
[6,29,2018,0,18,49,-0.39,-0.39,"2018-06-29T00:18:49",-0.45,-0.40500000000000014]
[6,29,2018,0,19,39,-0.33,-0.33,"2018-06-29T00:19:39",-0.36500000000000005,-0.42692307692307696]
[6,29,2018,0,20,39,-0.21000000000000002,-0.21000000000000002,"2018-06-29T00:20:39",-0.25,-0.39923076923076933]
[6,29,2018,0,21,29,-0.27,-0.27,"2018-06-29T00:21:29",-0.28000000000000003,-0.37038461538461542]
[6,29,2018,0,22,19,-0.18,-0.18,"2018-06-29T00:22:19",-0.16500000000000001,-0.2953846153846153]
[6,29,2018,0,22,29,-0.18,-0.18,"2018-06-29T00:22:29",-0.15,-0.2838461538461538]
[6,29,2018,0,23,19,-0.30000000000000004,-0.30000000000000004,"2018-06-29T00:23:19",-0.23500000000000001,-0.24923076923076914]
[6,29,2018,0,24,9,-0.48,-0.48,"2018-06-29T00:24:09",-0.39500000000000002,-0.26423076923076921]
[6,29,2018,0,25,9,-0.30000000000000004,-0.30000000000000004,"2018-06-29T00:25:09",-0.375,-0.2919230769230769]
[6,29,2018,0,25,59,-0.33,-0.33,"2018-06-29T00:25:59",-0.31500000000000006,-0.29884615384615382]
[6,29,2018,0,26,59,-0.30000000000000004,-0.30000000000000004,"2018-06-29T00:26:59",-0.33500000000000002,-0.34384615384615391]
[6,29,2018,0,27,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T00:27:49",-0.28500000000000003,-0.34615384615384615]
[6,29,2018,0,28,39,-0.33,-0.33,"2018-06-29T00:28:39",-0.32000000000000006,-0.32423076923076916]
[6,29,2018,0,29,29,-0.44999999999999996,-0.44999999999999996,"2018-06-29T00:29:29",-0.45999999999999996,-0.34846153846153843]
[6,29,2018,0,30,19,-0.33,-0.33,"2018-06-29T00:30:19",-0.36499999999999999,-0.35423076923076924]
[6,29,2018,0,31,9,-0.39,-0.39,"2018-06-29T00:31:09",-0.35000000000000003,-0.35653846153846158]
[6,29,2018,0,32,9,-0.24,-0.24,"2018-06-29T00:32:09",-0.29499999999999998,-0.35884615384615376]
[6,29,2018,0,32,59,-0.36,-0.36,"2018-06-29T00:32:59",-0.30499999999999999,-0.35769230769230764]
[6,29,2018,0,33,9,-0.30000000000000004,-0.30000000000000004,"2018-06-29T00:33:09",-0.315,-0.35076923076923072]
[6,29,2018,0,33,59,0.06,0.06,"2018-06-29T00:33:59",-0.14499999999999999,-0.27923076923076917]
[6,29,2018,0,34,49,0.06,0.06,"2018-06-29T00:34:49",6.5000000000000002E-2,-0.20538461538461542]
[6,29,2018,0,35,49,0,0,"2018-06-29T00:35:49",2.4999999999999998E-2,-0.11769230769230773]
[6,29,2018,0,36,39,-0.09,-0.09,"2018-06-29T00:36:39",-3.4999999999999996E-2,-7.3846153846153867E-2]
[6,29,2018,0,37,39,-0.33,-0.33,"2018-06-29T00:37:39",-0.30000000000000004,-7.0384615384615393E-2]
[6,29,2018,0,38,29,-0.36,-0.36,"2018-06-29T00:38:29",-0.35499999999999993,-0.13153846153846152]
[6,29,2018,0,39,19,-0.12,-0.12,"2018-06-29T00:39:19",-0.21000000000000005,-0.17653846153846153]
[6,29,2018,0,40,19,-0.06,-0.06,"2018-06-29T00:40:19",-0.11499999999999999,-0.2076923076923077]
[6,29,2018,0,41,9,0.06,0.06,"2018-06-29T00:41:09",0.02,-0.18115384615384617]
[6,29,2018,0,41,59,-0.09,-0.09,"2018-06-29T00:41:59",0.01,-0.12346153846153848]
[6,29,2018,0,42,59,0.24,0.24,"2018-06-29T00:42:59",0,-4.1538461538461531E-2]
[6,29,2018,0,43,39,0.30000000000000004,0.30000000000000004,"2018-06-29T00:43:39",0.27500000000000002,2.8846153846153862E-2]
[6,29,2018,0,43,49,0.15000000000000002,0.15000000000000002,"2018-06-29T00:43:49",0.27500000000000008,3.923076923076925E-2]
[6,29,2018,0,44,39,0,0,"2018-06-29T00:44:39",7.5000000000000011E-2,7.2692307692307709E-2]
[6,29,2018,0,45,29,0,0,"2018-06-29T00:45:29",0.01,6.807692307692309E-2]
[6,29,2018,0,46,29,0.24,0.24,"2018-06-29T00:46:29",0.19000000000000003,0.11653846153846155]
[6,29,2018,0,47,19,0.24,0.24,"2018-06-29T00:47:19",0.19999999999999998,0.14884615384615385]
[6,29,2018,0,48,9,0.03,0.03,"2018-06-29T00:48:09",0.15000000000000002,0.12000000000000001]
[6,29,2018,0,49,9,0.03,0.03,"2018-06-29T00:49:09",5.0000000000000001E-3,0.10961538461538461]
[6,29,2018,0,49,59,0,0,"2018-06-29T00:49:59",1.4999999999999999E-2,0.10846153846153841]
[6,29,2018,0,50,59,0,0,"2018-06-29T00:50:59",-5.0000000000000001E-3,5.7692307692307702E-2]
[6,29,2018,0,51,49,-0.06,-0.06,"2018-06-29T00:51:49",0,1.8461538461538467E-2]
[6,29,2018,0,52,39,-0.06,-0.06,"2018-06-29T00:52:39",-6.5000000000000002E-2,-1.0384615384615384E-2]
[6,29,2018,0,53,39,-0.06,-0.06,"2018-06-29T00:53:39",-0.01,-1.5000000000000003E-2]
[6,29,2018,0,54,29,-0.03,-0.03,"2018-06-29T00:54:29",-6.5000000000000002E-2,-2.8846153846153848E-2]
[6,29,2018,0,54,39,-0.03,-0.03,"2018-06-29T00:54:39",-0.06,-3.0000000000000002E-2]
[6,29,2018,0,55,29,-0.09,-0.09,"2018-06-29T00:55:29",-6.5000000000000002E-2,-4.2692307692307696E-2]
[6,29,2018,0,56,19,-0.42000000000000004,-0.42000000000000004,{"$f":"DATE(C5945,A5945,B5945)+TIME(D5945,E5945,F5945)","v":"2018-06-29T00:56:19"},-0.26,-9.6923076923076945E-2]
[6,29,2018,0,57,19,-0.39,-0.39,"2018-06-29T00:57:19",-0.39999999999999997,-0.18115384615384611]
[6,29,2018,0,58,9,-0.51,-0.51,"2018-06-29T00:58:09",-0.44500000000000001,-0.2607692307692307]
[6,29,2018,0,58,49,-0.63,-0.63,"2018-06-29T00:58:49",-0.55999999999999994,-0.3438461538461538]
[6,29,2018,0,59,49,-0.84000000000000008,-0.84000000000000008,"2018-06-29T00:59:49",-0.70500000000000007,-0.49153846153846154]
[6,29,2018,1,0,39,-0.72,-0.72,"2018-06-29T01:00:39",-0.77,-0.58038461538461539]
[6,29,2018,1,1,39,-0.57000000000000006,-0.57000000000000006,"2018-06-29T01:01:39",-0.625,-0.63230769230769235]
[6,29,2018,1,2,29,-0.27,-0.27,"2018-06-29T01:02:29",-0.34,-0.60115384615384637]
[6,29,2018,1,3,19,-0.27,-0.27,"2018-06-29T01:03:19",-0.28000000000000003,-0.5376923076923078]
[6,29,2018,1,4,19,-0.27,-0.27,"2018-06-29T01:04:19",-0.22499999999999998,-0.4211538461538461]
[6,29,2018,1,5,9,0,0,"2018-06-29T01:05:09",-0.12,-0.29884615384615382]
[6,29,2018,1,5,19,0,0,"2018-06-29T01:05:19",-7.4999999999999997E-2,-0.27461538461538459]
[6,29,2018,1,6,9,-0.24,-0.24,"2018-06-29T01:06:09",-9.5000000000000015E-2,-0.18923076923076926]
[6,29,2018,1,6,59,-0.36,-0.36,{"$f":"DATE(C6009,A6009,B6009)+TIME(D6009,E6009,F6009)","v":"2018-06-29T01:06:59"},-0.34,-0.20538461538461539]
[6,29,2018,1,7,59,-0.63,-0.63,"2018-06-29T01:07:59",-0.45999999999999996,-0.24807692307692308]
[6,29,2018,1,8,49,-0.60000000000000009,-0.60000000000000009,"2018-06-29T01:08:49",-0.65,-0.33115384615384613]
[6,29,2018,1,9,39,-0.42000000000000004,-0.42000000000000004,"2018-06-29T01:09:39",-0.52500000000000002,-0.42115384615384621]
[6,29,2018,1,10,39,-0.39,-0.39,"2018-06-29T01:10:39",-0.40000000000000008,-0.47884615384615398]
[6,29,2018,1,11,29,-0.18,-0.18,"2018-06-29T01:11:29",-0.255,-0.45115384615384629]
[6,29,2018,1,12,19,0,0,"2018-06-29T01:12:19",-6.5000000000000002E-2,-0.36807692307692302]
[6,29,2018,1,13,9,-0.18,-0.18,"2018-06-29T01:13:09",-7.0000000000000007E-2,-0.25846153846153841]
[6,29,2018,1,13,59,-0.12,-0.12,"2018-06-29T01:13:59",-0.19000000000000003,-0.19730769230769235]
[6,29,2018,1,14,59,-0.06,-0.06,"2018-06-29T01:14:59",-0.11499999999999999,-0.13153846153846155]
[6,29,2018,1,15,49,-0.18,-0.18,"2018-06-29T01:15:49",-0.14500000000000002,-0.11884615384615388]
[6,29,2018,1,16,39,-0.12,-0.12,"2018-06-29T01:16:39",-0.155,-0.13961538461538464]
[6,29,2018,1,16,49,-0.09,-0.09,"2018-06-29T01:16:49",-0.14000000000000001,-0.14423076923076925]
[6,29,2018,1,17,39,-0.21000000000000002,-0.21000000000000002,{"$f":"DATE(C6073,A6073,B6073)+TIME(D6073,E6073,F6073)","v":"2018-06-29T01:17:39"},-9.5000000000000015E-2,-0.13730769230769233]
[6,29,2018,1,18,39,-0.27,-0.27,"2018-06-29T01:18:39",-0.24,-0.15346153846153843]
[6,29,2018,1,19,29,-0.39,-0.39,"2018-06-29T01:19:29",-0.36500000000000005,-0.20769230769230768]
[6,29,2018,1,20,19,-0.30000000000000004,-0.30000000000000004,"2018-06-29T01:20:19",-0.34,-0.23653846153846153]
[6,29,2018,1,21,19,-0.42000000000000004,-0.42000000000000004,"2018-06-29T01:21:19",-0.38000000000000006,-0.29769230769230764]
[6,29,2018,1,22,9,-0.27,-0.27,"2018-06-29T01:22:09",-0.36499999999999999,-0.34153846153846151]
[6,29,2018,1,23,9,-0.24,-0.24,"2018-06-29T01:23:09",-0.27500000000000002,-0.34153846153846151]
[6,29,2018,1,23,59,-0.21000000000000002,-0.21000000000000002,"2018-06-29T01:23:59",-0.19500000000000003,-0.30230769230769233]
[6,29,2018,1,24,49,-0.12,-0.12,"2018-06-29T01:24:49",-0.24,-0.29076923076923078]
[6,29,2018,1,25,49,-0.03,-0.03,"2018-06-29T01:25:49",-7.4999999999999997E-2,-0.21346153846153845]
[6,29,2018,1,26,29,-0.09,-0.09,"2018-06-29T01:26:29",-5.4999999999999993E-2,-0.17307692307692304]
[6,29,2018,1,27,19,-0.21000000000000002,-0.21000000000000002,"2018-06-29T01:27:19",-0.14499999999999999,-0.14884615384615385]
[6,29,2018,1,27,29,-0.27,-0.27,"2018-06-29T01:27:29",-0.17500000000000002,-0.15]
[6,29,2018,1,28,19,-0.21000000000000002,-0.21000000000000002,{"$f":"DATE(C6137,A6137,B6137)+TIME(D6137,E6137,F6137)","v":"2018-06-29T01:28:19"},-0.27500000000000002,-0.16730769230769232]
[6,29,2018,1,29,19,-0.15000000000000002,-0.15000000000000002,"2018-06-29T01:29:19",-0.17,-0.15346153846153848]
[6,29,2018,1,30,9,-0.12,-0.12,"2018-06-29T01:30:09",-0.125,-0.16500000000000004]
[6,29,2018,1,30,59,-0.15000000000000002,-0.15000000000000002,"2018-06-29T01:30:59",-0.16,-0.18346153846153845]
[6,29,2018,1,31,59,-0.21000000000000002,-0.21000000000000002,"2018-06-29T01:31:59",-0.22999999999999998,-0.18923076923076926]
[6,29,2018,1,32,49,-0.33,-0.33,"2018-06-29T01:32:49",-0.22500000000000001,-0.18230769230769231]
[6,29,2018,1,33,39,-0.33,-0.33,"2018-06-29T01:33:39",-0.31000000000000005,-0.21115384615384616]
[6,29,2018,1,34,39,-0.33,-0.33,"2018-06-29T01:34:39",-0.35999999999999993,-0.26653846153846156]
[6,29,2018,1,35,29,-0.27,-0.27,"2018-06-29T01:35:29",-0.26500000000000001,-0.27923076923076923]
[6,29,2018,1,36,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T01:36:29",-0.31000000000000005,-0.29769230769230764]
[6,29,2018,1,37,19,-0.33,-0.33,"2018-06-29T01:37:19",-0.37000000000000005,-0.31961538461538452]
[6,29,2018,1,38,9,-0.36,-0.36,"2018-06-29T01:38:09",-0.35499999999999993,-0.32769230769230767]
[6,29,2018,1,38,19,-0.33,-0.33,"2018-06-29T01:38:19",-0.35499999999999998,-0.32653846153846156]
[6,29,2018,1,39,9,-0.33,-0.33,"2018-06-29T01:39:09",-0.33500000000000002,-0.32769230769230773]
[6,29,2018,1,40,9,-0.21000000000000002,-0.21000000000000002,"2018-06-29T01:40:09",-0.26,-0.32538461538461549]
[6,29,2018,1,40,59,-0.03,-0.03,"2018-06-29T01:40:59",-0.10000000000000002,-0.27692307692307694]
[6,29,2018,1,41,39,-0.06,-0.06,"2018-06-29T01:41:39",-4.5000000000000005E-2,-0.22846153846153838]
[6,29,2018,1,42,39,0.09,0.09,"2018-06-29T01:42:39",4.9999999999999996E-2,-0.13500000000000004]
[6,29,2018,1,43,29,-0.03,-0.03,"2018-06-29T01:43:29",5.0000000000000001E-3,-7.2692307692307723E-2]
[6,29,2018,1,44,19,-0.09,-0.09,"2018-06-29T01:44:19",-4.5000000000000005E-2,-3.0000000000000013E-2]
[6,29,2018,1,45,19,-0.21000000000000002,-0.21000000000000002,"2018-06-29T01:45:19",-0.13,-3.692307692307692E-2]
[6,29,2018,1,46,9,-0.24,-0.24,"2018-06-29T01:46:09",-0.215,-7.1538461538461537E-2]
[6,29,2018,1,47,9,-0.24,-0.24,"2018-06-29T01:47:09",-0.26,-0.14423076923076922]
[6,29,2018,1,47,59,-0.36,-0.36,"2018-06-29T01:47:59",-0.26499999999999996,-0.19038461538461543]
[6,29,2018,1,48,49,-0.44999999999999996,-0.44999999999999996,"2018-06-29T01:48:49",-0.45,-0.26999999999999996]
[6,29,2018,1,48,59,-0.48,-0.48,"2018-06-29T01:48:59",-0.47,-0.28500000000000009]
[6,29,2018,1,49,49,-0.51,-0.51,"2018-06-29T01:49:49",-0.48500000000000004,-0.34615384615384615]
[6,29,2018,1,50,49,-0.69000000000000006,-0.69000000000000006,"2018-06-29T01:50:49",-0.60500000000000009,-0.4326923076923076]
[6,29,2018,1,51,39,-0.69000000000000006,-0.69000000000000006,"2018-06-29T01:51:39",-0.70000000000000007,-0.52153846153846151]
[6,29,2018,1,52,29,-0.54,-0.54,"2018-06-29T01:52:29",-0.58500000000000008,-0.56769230769230772]
[6,29,2018,1,53,29,-0.33,-0.33,"2018-06-29T01:53:29",-0.39999999999999997,-0.55153846153846164]
[6,29,2018,1,54,19,-0.15000000000000002,-0.15000000000000002,"2018-06-29T01:54:19",-0.20999999999999996,-0.49153846153846159]
[6,29,2018,1,55,9,-0.09,-0.09,"2018-06-29T01:55:09",-0.08,-0.38423076923076932]
[6,29,2018,1,55,59,-0.27,-0.27,"2018-06-29T01:55:59",-0.20000000000000004,-0.2919230769230769]
[6,29,2018,1,56,49,-0.21000000000000002,-0.21000000000000002,"2018-06-29T01:56:49",-0.29000000000000004,-0.23999999999999996]
[6,29,2018,1,57,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T01:57:49",-0.23,-0.20076923076923084]
[6,29,2018,1,58,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T01:58:39",-0.29500000000000004,-0.22153846153846152]
[6,29,2018,1,59,29,-0.36,-0.36,"2018-06-29T01:59:29",-0.38999999999999996,-0.28730769230769232]
[6,29,2018,1,59,39,-0.36,-0.36,"2018-06-29T01:59:39",-0.39999999999999997,-0.29653846153846158]
[6,29,2018,2,0,29,-0.54,-0.54,"2018-06-29T02:00:29",-0.42499999999999999,-0.3323076923076923]
[6,29,2018,2,1,19,-0.66,-0.66,"2018-06-29T02:01:19",-0.57500000000000007,-0.39230769230769236]
[6,29,2018,2,2,19,-0.84000000000000008,-0.84000000000000008,"2018-06-29T02:02:19",-0.78500000000000003,-0.51576923076923076]
[6,29,2018,2,3,9,-0.63,-0.63,"2018-06-29T02:03:09",-0.72000000000000008,-0.58730769230769231]
[6,29,2018,2,4,9,-0.69000000000000006,-0.69000000000000006,"2018-06-29T02:04:09",-0.65,-0.64730769230769247]
[6,29,2018,2,4,59,-0.12,-0.12,"2018-06-29T02:04:59",-0.44500000000000001,-0.6311538461538464]
[6,29,2018,2,5,49,-0.06,-0.06,"2018-06-29T02:05:49",-5.000000000000001E-2,-0.52384615384615396]
[6,29,2018,2,6,49,0.06,0.06,"2018-06-29T02:06:49",-2.4999999999999998E-2,-0.34269230769230774]
[6,29,2018,2,7,39,0.27,0.27,"2018-06-29T02:07:39",0.16500000000000001,-0.17769230769230765]
[6,29,2018,2,8,39,0.33,0.33,"2018-06-29T02:08:39",0.25500000000000006,2.884615384615383E-2]
[6,29,2018,2,9,19,0.30000000000000004,0.30000000000000004,"2018-06-29T02:09:19",0.32500000000000001,0.13269230769230766]
[6,29,2018,2,10,9,0.24,0.24,"2018-06-29T02:10:09",0.27,0.1903846153846154]
[6,29,2018,2,10,19,0.21000000000000002,0.21000000000000002,"2018-06-29T02:10:19",0.255,0.19961538461538458]
[6,29,2018,2,11,9,0.15000000000000002,0.15000000000000002,"2018-06-29T02:11:09",0.17500000000000004,0.23653846153846153]
[6,29,2018,2,11,59,-0.09,-0.09,"2018-06-29T02:11:59",2.0000000000000004E-2,0.19961538461538467]
[6,29,2018,2,12,59,-0.69000000000000006,-0.69000000000000006,"2018-06-29T02:12:59",-0.35000000000000003,6.0000000000000005E-2]
[6,29,2018,2,13,49,-0.89999999999999991,-0.89999999999999991,"2018-06-29T02:13:49",-0.86499999999999988,-0.17423076923076927]
[6,29,2018,2,14,49,-0.99,-0.99,"2018-06-29T02:14:49",-0.91500000000000004,-0.43961538461538469]
[6,29,2018,2,15,39,-0.81,-0.81,"2018-06-29T02:15:39",-0.92500000000000016,-0.64500000000000013]
[6,29,2018,2,16,29,-0.27,-0.27,"2018-06-29T02:16:29",-0.47500000000000003,-0.7153846153846154]
[6,29,2018,2,17,29,0.03,0.03,"2018-06-29T02:17:29",-5.5000000000000014E-2,-0.61961538461538468]
[6,29,2018,2,18,19,0.30000000000000004,0.30000000000000004,"2018-06-29T02:18:19",0.19499999999999998,-0.39923076923076933]
[6,29,2018,2,19,19,0.30000000000000004,0.30000000000000004,"2018-06-29T02:19:19",0.30000000000000004,-0.11538461538461535]
[6,29,2018,2,20,9,0.06,0.06,"2018-06-29T02:20:09",0.18000000000000005,7.3846153846153867E-2]
[6,29,2018,2,20,59,-0.12,-0.12,"2018-06-29T02:20:59",-0.04,0.12692307692307692]
[6,29,2018,2,21,9,-0.18,-0.18,"2018-06-29T02:21:09",-0.08,0.12346153846153844]
[6,29,2018,2,21,59,-0.15000000000000002,-0.15000000000000002,"2018-06-29T02:21:59",-0.16,0.09]
[6,29,2018,2,22,49,-0.18,-0.18,"2018-06-29T02:22:49",-0.18999999999999997,1.153846153846157E-3]
[6,29,2018,2,23,49,-0.21000000000000002,-0.21000000000000002,"2018-06-29T02:23:49",-0.10999999999999999,-9.3461538461538457E-2]
[6,29,2018,2,24,29,-0.15000000000000002,-0.15000000000000002,"2018-06-29T02:24:29",-0.14499999999999999,-0.13500000000000004]
[6,29,2018,2,25,29,-0.06,-0.06,"2018-06-29T02:25:29",-4.5000000000000005E-2,-0.12692307692307689]
[6,29,2018,2,26,19,-0.21000000000000002,-0.21000000000000002,"2018-06-29T02:26:19",-0.14000000000000001,-0.12692307692307692]
[6,29,2018,2,27,9,-0.27,-0.27,"2018-06-29T02:27:09",-0.22500000000000001,-0.13269230769230769]
[6,29,2018,2,28,9,-0.66,-0.66,"2018-06-29T02:28:09",-0.46000000000000013,-0.21346153846153848]
[6,29,2018,2,28,59,-0.75,-0.75,"2018-06-29T02:28:59",-0.72000000000000008,-0.32538461538461544]
[6,29,2018,2,29,49,-0.86999999999999988,-0.86999999999999988,"2018-06-29T02:29:49",-0.82,-0.48115384615384615]
[6,29,2018,2,30,49,-0.84000000000000008,-0.84000000000000008,"2018-06-29T02:30:49",-0.89499999999999991,-0.65076923076923066]
[6,29,2018,2,31,39,-0.60000000000000009,-0.60000000000000009,"2018-06-29T02:31:39",-0.71500000000000019,-0.73499999999999999]
[6,29,2018,2,31,49,-0.36,-0.36,"2018-06-29T02:31:49",-0.63500000000000001,-0.73730769230769222]
[6,29,2018,2,32,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T02:32:39",-0.3,-0.68307692307692303]
[6,29,2018,2,33,29,-0.30000000000000004,-0.30000000000000004,"2018-06-29T02:33:29",-0.30000000000000004,-0.59538461538461551]
[6,29,2018,2,34,29,-0.44999999999999996,-0.44999999999999996,"2018-06-29T02:34:29",-0.48,-0.50653846153846149]
[6,29,2018,2,35,19,-0.39,-0.39,"2018-06-29T02:35:19",-0.39500000000000002,-0.41307692307692301]
[6,29,2018,2,36,19,-0.30000000000000004,-0.30000000000000004,"2018-06-29T02:36:19",-0.30499999999999999,{"$f":"AVERAGE(G6520:G6545)","v":-0.35538461538461541}]
[6,29,2018,2,37,9,-0.30000000000000004,-0.30000000000000004,"2018-06-29T02:37:09",-0.31000000000000005,-0.36115384615384627]
[6,29,2018,2,37,59,-0.27,-0.27,"2018-06-29T02:37:59",-0.22500000000000001,-0.34269230769230763]
[6,29,2018,2,38,49,-0.09,-0.09,"2018-06-29T02:38:49",-0.24500000000000002,-0.29076923076923072]
[6,29,2018,2,39,39,0,0,"2018-06-29T02:39:39",-2.4999999999999998E-2,-0.2192307692307692]
[6,29,2018,2,40,29,-0.06,-0.06,"2018-06-29T02:40:29",-2.4999999999999998E-2,-0.16615384615384615]
[6,29,2018,2,41,29,-0.18,-0.18,"2018-06-29T02:41:29",-0.12,-0.12230769230769228]
[6,29,2018,2,42,19,-0.51,-0.51,"2018-06-29T02:42:19",-0.36000000000000004,-0.15807692307692309]
[6,29,2018,2,42,29,-0.51,-0.51,"2018-06-29T02:42:29",-0.41500000000000004,-0.16846153846153847]
[6,29,2018,2,43,19,-0.42000000000000004,-0.42000000000000004,"2018-06-29T02:43:19",-0.42500000000000004,-0.20884615384615385]
[6,29,2018,2,44,9,-0.60000000000000009,-0.60000000000000009,"2018-06-29T02:44:09",-0.49500000000000005,-0.30461538461538462]
[6,29,2018,2,45,9,-0.48,-0.48,"2018-06-29T02:45:09",-0.53500000000000003,-0.41884615384615381]
[6,29,2018,2,45,59,-0.51,-0.51,"2018-06-29T02:45:59",-0.48999999999999994,-0.48115384615384615]
[6,29,2018,2,46,49,-0.60000000000000009,-0.60000000000000009,"2018-06-29T02:46:49",-0.505,-0.49153846153846154]
[6,29,2018,2,47,49,-0.36,-0.36,"2018-06-29T02:47:49",-0.48500000000000004,-0.50884615384615384]
[6,29,2018,2,48,39,-0.27,-0.27,"2018-06-29T02:48:39",-0.30000000000000004,-0.45923076923076928]
[6,29,2018,2,49,39,-0.27,-0.27,"2018-06-29T02:49:39",-0.23,-0.39346153846153853]
[6,29,2018,2,50,29,0.03,0.03,"2018-06-29T02:50:29",-4.9999999999999989E-2,-0.29884615384615382]
[6,29,2018,2,51,19,-0.24,-0.24,"2018-06-29T02:51:19",-9.9999999999999992E-2,-0.22384615384615386]
[6,29,2018,2,52,19,-0.06,-0.06,"2018-06-29T02:52:19",-0.12000000000000004,-0.15000000000000002]
[6,29,2018,2,52,29,-0.12,-0.12,"2018-06-29T02:52:29",-0.10000000000000002,-0.14307692307692307]
[6,29,2018,2,53,9,-0.15000000000000002,-0.15000000000000002,"2018-06-29T02:53:09",-0.13000000000000003,-0.1246153846153846]
[6,29,2018,2,53,59,-0.21000000000000002,-0.21000000000000002,"2018-06-29T02:53:59",-0.14000000000000001,-0.1073076923076923]
[6,29,2018,2,54,49,0,0,"2018-06-29T02:54:49",-0.18999999999999997,-0.14192307692307693]
[6,29,2018,2,55,49,-0.24,-0.24,"2018-06-29T02:55:49",-4.9999999999999996E-2,-0.12000000000000004]
[6,29,2018,2,56,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T02:56:39",-0.255,-0.15115384615384622]
[6,29,2018,2,57,29,-0.24,-0.24,"2018-06-29T02:57:29",-0.24,-0.16730769230769235]
[6,29,2018,2,58,29,-0.24,-0.24,"2018-06-29T02:58:29",-0.22,-0.18115384615384619]
[6,29,2018,2,59,19,-0.36,-0.36,"2018-06-29T02:59:19",-0.33,-0.22269230769230772]
[6,29,2018,3,0,19,-0.24,-0.24,"2018-06-29T03:00:19",-0.27499999999999997,-0.26538461538461544]
[6,29,2018,3,1,9,-0.33,-0.33,"2018-06-29T03:01:09",-0.28999999999999998,-0.27461538461538471]
[6,29,2018,3,1,59,-0.09,-0.09,"2018-06-29T03:01:59",-0.23500000000000001,-0.27230769230769231]
[6,29,2018,3,2,59,-0.18,-0.18,"2018-06-29T03:02:59",-0.10000000000000002,-0.24346153846153842]
[6,29,2018,3,3,49,0.09,0.09,"2018-06-29T03:03:49",-9.0000000000000024E-2,-0.18576923076923077]
[6,29,2018,3,3,59,0.15000000000000002,0.15000000000000002,"2018-06-29T03:03:59",-3.4999999999999996E-2,-0.16615384615384612]
[6,29,2018,3,4,49,0.03,0.03,"2018-06-29T03:04:49",0.14500000000000002,-9.2307692307692299E-2]
[6,29,2018,3,5,39,0,0,"2018-06-29T03:05:39",0.03,-2.6538461538461535E-2]
[6,29,2018,3,6,39,-0.18,-0.18,"2018-06-29T03:06:39",-9.5000000000000015E-2,-1.500000000000001E-2]
[6,29,2018,3,7,19,-0.21000000000000002,-0.21000000000000002,"2018-06-29T03:07:19",-0.18999999999999997,-2.8846153846153848E-2]
[6,29,2018,3,8,9,-0.42000000000000004,-0.42000000000000004,"2018-06-29T03:08:09",-0.31,-7.8461538461538458E-2]
[6,29,2018,3,9,9,-0.39,-0.39,"2018-06-29T03:09:09",-0.47500000000000003,-0.22153846153846149]
[6,29,2018,3,9,59,-0.36,-0.36,"2018-06-29T03:09:59",-0.34500000000000003,-0.2919230769230769]
[6,29,2018,3,10,59,-0.33,-0.33,"2018-06-29T03:10:59",-0.32500000000000001,-0.34500000000000003]
[6,29,2018,3,11,49,-0.27,-0.27,"2018-06-29T03:11:49",-0.30000000000000004,-0.35884615384615393]
[6,29,2018,3,12,39,-0.42000000000000004,-0.42000000000000004,"2018-06-29T03:12:39",-0.34,-0.35538461538461541]
[6,29,2018,3,13,39,-0.69000000000000006,-0.69000000000000006,"2018-06-29T03:13:39",-0.59499999999999997,-0.38884615384615384]
[6,29,2018,3,14,29,-0.78,-0.78,"2018-06-29T03:14:29",-0.74500000000000011,-0.4696153846153846]
[6,29,2018,3,15,19,-0.63,-0.63,"2018-06-29T03:15:19",-0.71499999999999997,-0.54230769230769227]
[6,29,2018,3,15,29,-0.60000000000000009,-0.60000000000000009,"2018-06-29T03:15:29",-0.68499999999999994,-0.55384615384615377]
[6,29,2018,3,16,19,-0.15000000000000002,-0.15000000000000002,"2018-06-29T03:16:19",-0.33,-0.55153846153846153]
[6,29,2018,3,17,19,-0.06,-0.06,"2018-06-29T03:17:19",-0.13,-0.4834615384615385]
[6,29,2018,3,18,9,0.27,0.27,"2018-06-29T03:18:09",9.9999999999999992E-2,-0.33346153846153848]
[6,29,2018,3,18,59,0.15000000000000002,0.15000000000000002,"2018-06-29T03:18:59",0.25,{"$f":"AVERAGE(G6776:G6801)","v":-0.13846153846153847}]
[6,29,2018,3,19,59,-0.03,-0.03,"2018-06-29T03:19:59",0.02,1.384615384615385E-2]
[6,29,2018,3,20,49,-0.09,-0.09,"2018-06-29T03:20:49",-9.9999999999999992E-2,3.0000000000000006E-2]
[6,29,2018,3,21,39,-0.27,-0.27,"2018-06-29T03:21:39",-0.20499999999999999,1.153846153846155E-2]
[6,29,2018,3,22,29,-0.39,-0.39,"2018-06-29T03:22:29",-0.39000000000000007,-9.3461538461538471E-2]
[6,29,2018,3,23,19,-0.48,-0.48,"2018-06-29T03:23:19",-0.42,-0.22269230769230766]
[6,29,2018,3,24,19,-0.42000000000000004,-0.42000000000000004,"2018-06-29T03:24:19",-0.46500000000000002,-0.33461538461538465]
[6,29,2018,3,25,9,-0.39,-0.39,"2018-06-29T03:25:09",-0.38500000000000001,-0.38538461538461544]
[6,29,2018,3,25,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T03:25:59",-0.43,-0.42576923076923073]
[6,29,2018,3,26,9,-0.44999999999999996,-0.44999999999999996,"2018-06-29T03:26:09",-0.43999999999999995,-0.42692307692307685]
[6,29,2018,3,26,59,-0.36,-0.36,"2018-06-29T03:26:59",-0.39499999999999996,-0.42230769230769216]
[6,29,2018,3,27,59,-0.42000000000000004,-0.42000000000000004,"2018-06-29T03:27:59",-0.38999999999999996,-0.40730769230769232]
[6,29,2018,3,28,49,-0.54,-0.54,"2018-06-29T03:28:49",-0.48500000000000004,-0.41884615384615387]
[6,29,2018,3,29,39,-0.51,-0.51,"2018-06-29T03:29:39",-0.54,{"$f":"AVERAGE(G6840:G6865)","v":-0.44884615384615378}]
[6,29,2018,3,30,39,-0.36,-0.36,"2018-06-29T03:30:39",-0.40499999999999997,-0.44076923076923075]
[6,29,2018,3,31,29,-0.36,-0.36,"2018-06-29T03:31:29",-0.34499999999999997,-0.43499999999999994]
[6,29,2018,3,32,29,-0.24,-0.24,"2018-06-29T03:32:29",-0.29499999999999998,-0.41076923076923078]
[6,29,2018,3,33,19,-0.15000000000000002,-0.15000000000000002,"2018-06-29T03:33:19",-0.18499999999999997,-0.34269230769230774]
[6,29,2018,3,34,9,-0.33,-0.33,"2018-06-29T03:34:09",-0.23,-0.29076923076923084]
[6,29,2018,3,35,9,-0.48,-0.48,"2018-06-29T03:35:09",-0.38000000000000006,-0.28961538461538466]
[6,29,2018,3,35,19,-0.54,-0.54,"2018-06-29T03:35:19",-0.42,-0.29769230769230764]
[6,29,2018,3,36,39,-0.75,-0.75,"2018-06-29T03:36:39",-0.66500000000000004,-0.39692307692307693]
[6,29,2018,3,36,49,-0.72,-0.72,"2018-06-29T03:36:49",-0.68,-0.41538461538461546]
[6,29,2018,3,37,39,-0.63,-0.63,"2018-06-29T03:37:39",-0.69499999999999995,-0.5146153846153847]
[6,29,2018,3,38,39,-0.60000000000000009,-0.60000000000000009,"2018-06-29T03:38:39",-0.64500000000000002,-0.60461538461538467]
[6,29,2018,3,39,29,-0.60000000000000009,-0.60000000000000009,"2018-06-29T03:39:29",-0.58500000000000008,-0.64038461538461544]
[6,29,2018,3,40,19,-0.33,-0.33,"2018-06-29T03:40:19",-0.41500000000000004,{"$f":"AVERAGE(G6904:G6929)","v":-0.59884615384615392}]
[6,29,2018,3,41,19,-0.63,-0.63,"2018-06-29T03:41:19",-0.52,-0.55730769230769228]
[6,29,2018,3,42,9,-0.63,-0.63,"2018-06-29T03:42:09",-0.65,-0.55384615384615399]
[6,29,2018,3,42,59,-0.48,-0.48,"2018-06-29T03:42:59",-0.57499999999999996,-0.53884615384615386]
[6,29,2018,3,43,59,-0.18,-0.18,"2018-06-29T03:43:59",-0.32999999999999996,-0.48115384615384627]
[6,29,2018,3,44,49,-0.12,-0.12,"2018-06-29T03:44:49",-0.08,-0.42923076923076925]
[6,29,2018,3,45,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T03:45:49",-0.215,-0.34730769230769226]
[6,29,2018,3,46,39,-0.27,-0.27,"2018-06-29T03:46:39",-0.29500000000000004,-0.27807692307692311]
[6,29,2018,3,47,29,-0.21000000000000002,-0.21000000000000002,"2018-06-29T03:47:29",-0.23499999999999999,-0.2203846153846154]
[6,29,2018,3,47,39,-0.21000000000000002,-0.21000000000000002,"2018-06-29T03:47:39",{"$f":"AVERAGE(G6968:G6973)","v":-0.22499999999999998},-0.21346153846153845]
[6,29,2018,3,48,29,-0.03,-0.03,"2018-06-29T03:48:29",-7.5000000000000011E-2,-0.17538461538461536]
[6,29,2018,3,49,29,-0.15000000000000002,-0.15000000000000002,"2018-06-29T03:49:29",-0.17499999999999996,-0.19730769230769238]
[6,29,2018,3,50,9,-0.15000000000000002,-0.15000000000000002,"2018-06-29T03:50:09",-0.17499999999999996,-0.18461538461538465]
[6,29,2018,3,50,59,-0.03,-0.03,"2018-06-29T03:50:59",-0.14000000000000001,{"$f":"AVERAGE(G6968:G6993)","v":-0.15461538461538463}]
[6,29,2018,3,51,59,-0.24,-0.24,"2018-06-29T03:51:59",-0.13,-0.13269230769230766]
[6,29,2018,3,52,49,-0.24,-0.24,"2018-06-29T03:52:49",-0.25,-0.1719230769230769]
[6,29,2018,3,53,39,-0.21000000000000002,-0.21000000000000002,"2018-06-29T03:53:39",-0.25,-0.1857692307692308]
[6,29,2018,3,54,39,-0.15000000000000002,-0.15000000000000002,"2018-06-29T03:54:39",-0.17500000000000004,-0.18692307692307694]
[6,29,2018,3,55,29,0,0,"2018-06-29T03:55:29",-1.5000000000000005E-2,-0.16384615384615384]
[6,29,2018,3,56,29,-0.09,-0.09,"2018-06-29T03:56:29",-2.4999999999999998E-2,-0.13153846153846155]
[6,29,2018,3,57,19,-0.09,-0.09,"2018-06-29T03:57:19",-9.9999999999999992E-2,-0.10038461538461536]
[6,29,2018,3,58,9,-0.33,-0.33,"2018-06-29T03:58:09",-0.21000000000000005,-0.10038461538461542]
[6,29,2018,3,58,19,-0.39,-0.39,"2018-06-29T03:58:19",{"$f":"AVERAGE(G7032:G7037)","v":-0.26},-0.10846153846153847]
[6,29,2018,3,59,9,-0.42000000000000004,-0.42000000000000004,"2018-06-29T03:59:09",-0.40499999999999997,-0.16153846153846155]
[6,29,2018,3,59,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T03:59:59",-0.4200000000000001,-0.2446153846153846]
[6,29,2018,4,0,59,-0.36,-0.36,"2018-06-29T04:00:59",-0.4549999999999999,-0.33923076923076917]
[6,29,2018,4,1,49,-0.33,-0.33,"2018-06-29T04:01:49",-0.30499999999999999,-0.37730769230769234]
[6,29,2018,4,2,49,-0.36,-0.36,"2018-06-29T04:02:49",-0.315,-0.37961538461538474]
[6,29,2018,4,3,39,-0.36,-0.36,"2018-06-29T04:03:39",-0.36499999999999999,-0.36923076923076914]
[6,29,2018,4,4,39,-0.33,-0.33,"2018-06-29T04:04:39",-0.34,-0.34615384615384615]
[6,29,2018,4,5,19,-0.30000000000000004,-0.30000000000000004,"2018-06-29T04:05:19",-0.32500000000000001,-0.32769230769230773]
[6,29,2018,4,6,9,-0.33,-0.33,"2018-06-29T04:06:09",-0.31500000000000006,-0.3323076923076923]
[6,29,2018,4,7,9,-0.21000000000000002,-0.21000000000000002,"2018-06-29T04:07:09",-0.29499999999999998,-0.32769230769230773]
[6,29,2018,4,7,59,-0.03,-0.03,"2018-06-29T04:07:59",-9.5000000000000015E-2,-0.27115384615384619]
[6,29,2018,4,8,49,0.03,0.03,"2018-06-29T04:08:49",-4.5000000000000005E-2,-0.21461538461538462]
[6,29,2018,4,8,59,0,0,"2018-06-29T04:08:59",{"$f":"AVERAGE(G7096:G7101)","v":-0.04},-0.20192307692307698]
[6,29,2018,4,9,49,-0.12,-0.12,"2018-06-29T04:09:49",-0.04,-0.14999999999999994]
[6,29,2018,4,10,39,-0.15000000000000002,-0.15000000000000002,"2018-06-29T04:10:39",-0.125,-0.11192307692307692]
[6,29,2018,4,11,39,-0.03,-0.03,"2018-06-29T04:11:39",-9.5000000000000015E-2,-7.3846153846153867E-2]
[6,29,2018,4,12,29,-0.09,-0.09,"2018-06-29T04:12:29",-3.4999999999999996E-2,-7.0384615384615407E-2]
[6,29,2018,4,13,29,-0.66,-0.66,"2018-06-29T04:13:29",-0.41,-0.1557692307692308]
[6,29,2018,4,14,19,-0.60000000000000009,-0.60000000000000009,"2018-06-29T04:14:19",-0.63,-0.26423076923076927]
[6,29,2018,4,15,9,-0.57000000000000006,-0.57000000000000006,"2018-06-29T04:15:09",-0.57500000000000007,-0.34730769230769237]
[6,29,2018,4,16,9,-0.39,-0.39,"2018-06-29T04:16:09",-0.48000000000000004,-0.4407692307692308]
[6,29,2018,4,16,59,-0.21000000000000002,-0.21000000000000002,"2018-06-29T04:16:59",-0.26500000000000001,-0.47423076923076923]
[6,29,2018,4,17,59,-0.03,-0.03,"2018-06-29T04:17:59",-0.14000000000000001,-0.39230769230769236]
[6,29,2018,4,18,9,-0.03,-0.03,"2018-06-29T04:18:09",-0.11500000000000003,-0.37038461538461542]
[6,29,2018,4,19,29,-0.21000000000000002,-0.21000000000000002,"2018-06-29T04:19:29",-0.18500000000000003,-0.24000000000000005]
[6,29,2018,4,19,39,-0.24,-0.24,"2018-06-29T04:19:39",{"$f":"AVERAGE(G7160:G7165)","v":-0.19999999999999998},-0.22846153846153852]
[6,29,2018,4,20,29,-0.39,-0.39,"2018-06-29T04:20:29",-0.36000000000000004,-0.21230769230769223]
[6,29,2018,4,21,19,-0.30000000000000004,-0.30000000000000004,"2018-06-29T04:21:19",-0.33,-0.22730769230769232]
[6,29,2018,4,22,19,-0.09,-0.09,"2018-06-29T04:22:19",-0.16,-0.2319230769230769]
[6,29,2018,4,23,9,-0.09,-0.09,"2018-06-29T04:23:09",-0.08,-0.22730769230769232]
[6,29,2018,4,24,9,-0.24,-0.24,"2018-06-29T04:24:09",-0.23,-0.22615384615384618]
[6,29,2018,4,24,59,-0.33,-0.33,"2018-06-29T04:24:59",-0.27,-0.20538461538461542]
[6,29,2018,4,25,49,-0.12,-0.12,"2018-06-29T04:25:49",-0.27500000000000008,-0.19846153846153847]
[6,29,2018,4,26,49,-0.03,-0.03,"2018-06-29T04:26:49",-0.08,-0.18576923076923074]
[6,29,2018,4,27,39,-0.15000000000000002,-0.15000000000000002,"2018-06-29T04:27:39",-8.5000000000000006E-2,-0.18692307692307686]
[6,29,2018,4,28,29,-0.39,-0.39,"2018-06-29T04:28:29",-0.34500000000000003,-0.21461538461538462]
[6,29,2018,4,29,29,-0.33,-0.33,"2018-06-29T04:29:29",-0.33,-0.22615384615384618]
[6,29,2018,4,30,19,-0.18,-0.18,"2018-06-29T04:30:19",{"$f":"AVERAGE(G7224:G7229)","v":-0.23499999999999999},-0.22384615384615383]
[6,29,2018,4,30,29,-0.21000000000000002,-0.21000000000000002,"2018-06-29T04:30:29",-0.21499999999999997,-0.22846153846153844]
[6,29,2018,4,31,19,-0.24,-0.24,"2018-06-29T04:31:19",-0.19499999999999998,-0.25269230769230766]
[6,29,2018,4,32,19,-0.60000000000000009,-0.60000000000000009,"2018-06-29T04:32:19",-0.47500000000000003,-0.31846153846153852]
[6,29,2018,4,32,59,-0.36,-0.36,"2018-06-29T04:32:59",-0.505,-0.33]
[6,29,2018,4,33,49,-0.24,-0.24,"2018-06-29T04:33:49",-0.22500000000000001,-0.3057692307692309]
[6,29,2018,4,34,49,-0.09,-0.09,"2018-06-29T04:34:49",-0.22,-0.30692307692307702]
[6,29,2018,4,35,39,-0.18,-0.18,"2018-06-29T04:35:39",-0.13500000000000001,-0.29769230769230776]
[6,29,2018,4,36,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T04:36:29",-0.39500000000000002,-0.29538461538461547]
[6,29,2018,4,37,29,-0.44999999999999996,-0.44999999999999996,"2018-06-29T04:37:29",-0.47499999999999992,-0.30000000000000004]
[6,29,2018,4,38,19,-0.54,-0.54,"2018-06-29T04:38:19",-0.53500000000000003,-0.36923076923076914]
[6,29,2018,4,39,9,-0.48,-0.48,"2018-06-29T04:39:09",-0.52500000000000002,-0.42807692307692297]
[6,29,2018,4,40,9,-0.24,-0.24,"2018-06-29T04:40:09",-0.36999999999999994,-0.47307692307692295]
[6,29,2018,4,40,59,-0.15000000000000002,-0.15000000000000002,"2018-06-29T04:40:59",{"$f":"AVERAGE(G7288:G7293)","v":-0.20999999999999996},-0.41769230769230781]
[6,29,2018,4,41,9,-0.15000000000000002,-0.15000000000000002,"2018-06-29T04:41:09",-0.19499999999999998,-0.40500000000000014]
[6,29,2018,4,41,59,-0.21000000000000002,-0.21000000000000002,"2018-06-29T04:41:59",-0.14500000000000002,-0.3461538461538462]
[6,29,2018,4,42,49,-0.21000000000000002,-0.21000000000000002,"2018-06-29T04:42:49",-0.215,-0.27923076923076928]
[6,29,2018,4,43,49,-0.27,-0.27,"2018-06-29T04:43:49",-0.27,-0.22615384615384612]
[6,29,2018,4,44,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T04:44:39",-0.28000000000000003,-0.22153846153846149]
[6,29,2018,4,45,29,-0.24,-0.24,"2018-06-29T04:45:29",-0.24,-0.22961538461538461]
[6,29,2018,4,46,29,-0.54,-0.54,"2018-06-29T04:46:29",-0.40000000000000008,-0.2861538461538462]
[6,29,2018,4,47,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T04:47:29",-0.53500000000000014,-0.35653846153846164]
[6,29,2018,4,48,9,-0.57000000000000006,-0.57000000000000006,"2018-06-29T04:48:09",-0.57500000000000018,-0.40269230769230779]
[6,29,2018,4,48,59,-0.57000000000000006,-0.57000000000000006,"2018-06-29T04:48:59",-0.56000000000000005,-0.45576923076923076]
[6,29,2018,4,49,49,-0.54,-0.54,"2018-06-29T04:49:49",-0.56500000000000006,-0.52038461538461533]
[6,29,2018,4,50,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T04:50:49",-0.51,-0.54576923076923078]
[6,29,2018,4,51,39,-0.42000000000000004,-0.42000000000000004,"2018-06-29T04:51:39",{"$f":"AVERAGE(G7352:G7357)","v":-0.43999999999999995},-0.5296153846153846]
[6,29,2018,4,51,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T04:51:49",-0.44,-0.52384615384615385]
[6,29,2018,4,52,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T04:52:39",-0.34500000000000003,-0.47769230769230769]
[6,29,2018,4,53,29,-0.39,-0.39,"2018-06-29T04:53:29",-0.32000000000000006,-0.43038461538461542]
[6,29,2018,4,54,29,-0.27,-0.27,"2018-06-29T04:54:29",-0.27,-0.36461538461538462]
[6,29,2018,4,55,19,-0.48,-0.48,"2018-06-29T04:55:19",-0.33500000000000002,-0.33923076923076922]
[6,29,2018,4,56,9,-0.54,-0.54,"2018-06-29T04:56:09",-0.49499999999999994,-0.35076923076923083]
[6,29,2018,4,57,9,-0.75,-0.75,"2018-06-29T04:57:09",-0.60499999999999998,-0.41653846153846152]
[6,29,2018,4,57,59,-0.75,-0.75,"2018-06-29T04:57:59",-0.76500000000000012,-0.49615384615384606]
[6,29,2018,4,58,59,-0.57000000000000006,-0.57000000000000006,"2018-06-29T04:58:59",-0.68500000000000005,-0.59769230769230763]
[6,29,2018,4,59,49,-0.36,-0.36,"2018-06-29T04:59:49",-0.48499999999999993,-0.61384615384615382]
[6,29,2018,5,0,39,-0.12,-0.12,"2018-06-29T05:00:39",-0.25499999999999995,-0.5607692307692308]
[6,29,2018,5,0,59,-0.12,-0.12,"2018-06-29T05:00:59",-0.18000000000000002,-0.53076923076923066]
[6,29,2018,5,2,19,-0.09,-0.09,"2018-06-29T05:02:19",{"$f":"AVERAGE(G7416:G7421)","v":-8.5000000000000006E-2},-0.33230769230769225]
[6,29,2018,5,2,29,-0.12,-0.12,"2018-06-29T05:02:29",-7.4999999999999997E-2,-0.30692307692307697]
[6,29,2018,5,3,19,-0.39,-0.39,"2018-06-29T05:03:19",-0.29499999999999998,-0.24230769230769234]
[6,29,2018,5,4,9,-0.44999999999999996,-0.44999999999999996,"2018-06-29T05:04:09",-0.41500000000000004,-0.23307692307692307]
[6,29,2018,5,5,9,-0.36,-0.36,"2018-06-29T05:05:09",-0.42,-0.28038461538461545]
[6,29,2018,5,5,59,-0.30000000000000004,-0.30000000000000004,"2018-06-29T05:05:59",-0.31,-0.30923076923076931]
[6,29,2018,5,6,49,-0.27,-0.27,"2018-06-29T05:06:49",-0.29000000000000004,-0.35423076923076924]
[6,29,2018,5,7,49,-0.06,-0.06,"2018-06-29T05:07:49",-0.21,-0.32423076923076921]
[6,29,2018,5,8,39,-0.03,-0.03,"2018-06-29T05:08:39",-4.5000000000000005E-2,-0.24923076923076917]
[6,29,2018,5,9,39,-0.15000000000000002,-0.15000000000000002,"2018-06-29T05:09:39",-0.15,-0.19153846153846163]
[6,29,2018,5,10,29,-0.03,-0.03,"2018-06-29T05:10:29",-1.5000000000000005E-2,-0.13269230769230769]
[6,29,2018,5,11,19,-0.39,-0.39,"2018-06-29T05:11:19",-0.28000000000000003,-0.14307692307692307]
[6,29,2018,5,12,19,-0.21000000000000002,-0.21000000000000002,{"$f":"DATE(C7481,A7481,B7481)+TIME(D7481,E7481,F7481)","v":"2018-06-29T05:12:19"},-0.19500000000000003,-0.14769230769230773]
[6,29,2018,5,13,9,-0.60000000000000009,-0.60000000000000009,"2018-06-29T05:13:09",-0.4200000000000001,-0.22269230769230772]
[6,29,2018,5,13,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T05:13:59",-0.56999999999999995,-0.3034615384615385]
[6,29,2018,5,14,9,-0.39,-0.39,"2018-06-29T05:14:09",-0.53500000000000003,-0.31846153846153852]
[6,29,2018,5,14,59,-0.60000000000000009,-0.60000000000000009,"2018-06-29T05:14:59",-0.48000000000000004,-0.41307692307692317]
[6,29,2018,5,16,9,-0.33,-0.33,"2018-06-29T05:16:09",-0.49500000000000005,-0.46500000000000008]
[6,29,2018,5,16,39,-0.36,-0.36,"2018-06-29T05:16:39",-0.36499999999999999,-0.4869230769230769]
[6,29,2018,5,17,29,-0.15000000000000002,-0.15000000000000002,"2018-06-29T05:17:29",-0.29499999999999998,-0.45230769230769236]
[6,29,2018,5,18,29,-0.24,-0.24,"2018-06-29T05:18:29",-0.15,-0.3634615384615385]
[6,29,2018,5,19,19,-0.42000000000000004,-0.42000000000000004,"2018-06-29T05:19:19",-0.35499999999999998,-0.34038461538461545]
[6,29,2018,5,20,19,-0.30000000000000004,-0.30000000000000004,"2018-06-29T05:20:19",-0.31,-0.28615384615384615]
[6,29,2018,5,21,9,-0.27,-0.27,"2018-06-29T05:21:09",-0.27500000000000002,-0.26999999999999996]
[6,29,2018,5,21,59,-0.12,-0.12,"2018-06-29T05:21:59",-0.24000000000000007,-0.27115384615384613]
[6,29,2018,5,22,59,-0.21000000000000002,-0.21000000000000002,{"$f":"DATE(C7545,A7545,B7545)+TIME(D7545,E7545,F7545)","v":"2018-06-29T05:22:59"},-7.5000000000000011E-2,-0.24807692307692308]
[6,29,2018,5,23,49,-0.06,-0.06,"2018-06-29T05:23:49",-0.19500000000000003,-0.20884615384615385]
[6,29,2018,5,24,39,-0.03,-0.03,"2018-06-29T05:24:39",-4.5000000000000005E-2,-0.15923076923076923]
[6,29,2018,5,24,49,-0.24,-0.24,"2018-06-29T05:24:49",-7.4999999999999997E-2,-0.15692307692307692]
[6,29,2018,5,25,39,-0.36,-0.36,"2018-06-29T05:25:39",-0.30499999999999999,-0.16730769230769232]
[6,29,2018,5,26,39,-0.18,-0.18,"2018-06-29T05:26:39",-0.25999999999999995,-0.18923076923076923]
[6,29,2018,5,27,29,-0.27,-0.27,"2018-06-29T05:27:29",-0.21,-0.20884615384615385]
[6,29,2018,5,28,19,-0.21000000000000002,-0.21000000000000002,"2018-06-29T05:28:19",-0.21,-0.21692307692307694]
[6,29,2018,5,29,19,-0.33,-0.33,"2018-06-29T05:29:19",-0.28000000000000003,-0.25500000000000006]
[6,29,2018,5,30,19,-0.42000000000000004,-0.42000000000000004,"2018-06-29T05:30:19",-0.37000000000000005,-0.26307692307692304]
[6,29,2018,5,30,59,-0.33,-0.33,"2018-06-29T05:30:59",-0.38999999999999996,-0.28846153846153844]
[6,29,2018,5,31,49,-0.51,-0.51,"2018-06-29T05:31:49",-0.36000000000000004,-0.31730769230769229]
[6,29,2018,5,32,39,-0.42000000000000004,-0.42000000000000004,"2018-06-29T05:32:39",-0.44999999999999996,-0.36346153846153845]
[6,29,2018,5,33,39,-0.21000000000000002,-0.21000000000000002,{"$f":"DATE(C7609,A7609,B7609)+TIME(D7609,E7609,F7609)","v":"2018-06-29T05:33:39"},-0.22500000000000001,-0.35076923076923094]
[6,29,2018,5,34,29,-0.36,-0.36,"2018-06-29T05:34:29",-0.33,-0.34961538461538455]
[6,29,2018,5,35,19,0.27,0.27,"2018-06-29T05:35:19",-4.9999999999999968E-2,-0.27230769230769231]
[6,29,2018,5,35,29,0.12,0.12,"2018-06-29T05:35:29",3.0000000000000009E-2,-0.25500000000000006]
[6,29,2018,5,36,19,-0.09,-0.09,"2018-06-29T05:36:19",1.4999999999999999E-2,-0.17999999999999997]
[6,29,2018,5,37,19,-0.24,-0.24,"2018-06-29T05:37:19",-0.215,-0.14538461538461539]
[6,29,2018,5,38,9,-0.12,-0.12,"2018-06-29T05:38:09",-0.20499999999999999,-0.13615384615384618]
[6,29,2018,5,38,59,0.09,0.09,"2018-06-29T05:38:59",-2.5000000000000008E-2,-7.0384615384615379E-2]
[6,29,2018,5,39,59,-0.06,-0.06,"2018-06-29T05:39:59",-5.0000000000000001E-3,-9.2307692307692299E-2]
[6,29,2018,5,40,49,-0.24,-0.24,"2018-06-29T05:40:49",-0.105,-0.10846153846153844]
[6,29,2018,5,41,39,-0.27,-0.27,"2018-06-29T05:41:39",-0.22,-0.10384615384615385]
[6,29,2018,5,42,39,-0.39,-0.39,"2018-06-29T05:42:39",-0.39500000000000007,-0.15346153846153848]
[6,29,2018,5,43,29,-0.12,-0.12,"2018-06-29T05:43:29",-0.22500000000000001,-0.1973076923076923]
[6,29,2018,5,43,49,-0.18,-0.18,"2018-06-29T05:43:49",-0.16,-0.20884615384615388]
[6,29,2018,5,45,9,-0.30000000000000004,-0.30000000000000004,"2018-06-29T05:45:09",-0.22,-0.24346153846153851]
[6,29,2018,5,45,59,-0.36,-0.36,"2018-06-29T05:45:59",-0.33,-0.26653846153846156]
[6,29,2018,5,46,9,-0.15000000000000002,-0.15000000000000002,"2018-06-29T05:46:09",-0.30499999999999999,-0.25615384615384618]
[6,29,2018,5,46,59,-0.33,-0.33,"2018-06-29T05:46:59",-0.28500000000000003,-0.24115384615384622]
[6,29,2018,5,47,59,-0.36,-0.36,"2018-06-29T05:47:59",-0.43,-0.29769230769230776]
[6,29,2018,5,48,49,-0.03,-0.03,"2018-06-29T05:48:49",-0.23,-0.31269230769230766]
[6,29,2018,5,49,39,-0.27,-0.27,"2018-06-29T05:49:39",-9.5000000000000015E-2,-0.27692307692307688]
[6,29,2018,5,50,39,-0.21000000000000002,-0.21000000000000002,"2018-06-29T05:50:39",-0.245,-0.26653846153846161]
[6,29,2018,5,51,29,0.09,0.09,"2018-06-29T05:51:29",2.4999999999999994E-2,-0.18576923076923085]
[6,29,2018,5,52,19,-0.36,-0.36,"2018-06-29T05:52:19",-0.18499999999999997,-0.14884615384615388]
[6,29,2018,5,53,19,-0.66,-0.66,"2018-06-29T05:53:19",-0.58000000000000007,-0.24115384615384614]
[6,29,2018,5,54,9,-0.57000000000000006,-0.57000000000000006,"2018-06-29T05:54:09",-0.55000000000000016,-0.31269230769230771]
[6,29,2018,5,55,9,-0.63,-0.63,"2018-06-29T05:55:09",-0.71499999999999997,-0.43153846153846154]
[6,29,2018,5,55,59,0.06,0.06,"2018-06-29T05:55:59",-0.38999999999999996,-0.51230769230769235]
[6,29,2018,5,56,49,-0.21000000000000002,-0.21000000000000002,"2018-06-29T05:56:49",-0.08,-0.47076923076923077]
[6,29,2018,5,56,59,-0.27,-0.27,"2018-06-29T05:56:59",-0.13500000000000001,-0.46384615384615385]
[6,29,2018,5,57,49,-0.15000000000000002,-0.15000000000000002,"2018-06-29T05:57:49",-0.22999999999999998,-0.38423076923076932]
[6,29,2018,5,58,59,-0.30000000000000004,-0.30000000000000004,"2018-06-29T05:58:59",-0.08,{"$f":"AVERAGE(G7736:G7761)","v":-0.24000000000000005}]
[6,29,2018,5,59,29,-0.21000000000000002,-0.21000000000000002,"2018-06-29T05:59:29",-0.20499999999999999,-0.18923076923076926]
[6,29,2018,6,0,19,-0.33,-0.33,"2018-06-29T06:00:19",-0.28500000000000003,-0.18115384615384617]
[6,29,2018,6,1,19,-0.15000000000000002,-0.15000000000000002,"2018-06-29T06:01:19",-5.000000000000001E-2,-0.16153846153846155]
[6,29,2018,6,2,9,-0.21000000000000002,-0.21000000000000002,"2018-06-29T06:02:09",-0.155,-0.14884615384615382]
[6,29,2018,6,2,59,-0.21000000000000002,-0.21000000000000002,"2018-06-29T06:02:59",-0.22,-0.18923076923076926]
[6,29,2018,6,3,59,-0.39,-0.39,"2018-06-29T06:03:59",-0.24500000000000002,-0.19153846153846152]
[6,29,2018,6,4,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T06:04:49",-0.48,-0.22615384615384615]
[6,29,2018,6,5,49,-0.44999999999999996,-0.44999999999999996,"2018-06-29T06:05:49",-0.42499999999999999,-0.32076923076923075]
[6,29,2018,6,6,39,-0.66,-0.66,"2018-06-29T06:06:39",-0.62,-0.41076923076923078]
[6,29,2018,6,7,29,-0.63,-0.63,"2018-06-29T06:07:29",-0.64499999999999991,-0.49846153846153851]
[6,29,2018,6,7,39,-0.60000000000000009,-0.60000000000000009,"2018-06-29T06:07:39",-0.63500000000000001,-0.51923076923076927]
[6,29,2018,6,8,29,-0.18,-0.18,"2018-06-29T06:08:29",-0.37000000000000005,-0.51]
[6,29,2018,6,9,19,-0.33,-0.33,"2018-06-29T06:09:19",-0.20500000000000004,-0.45692307692307704]
[6,29,2018,6,10,19,-0.39,-0.39,"2018-06-29T06:10:19",-0.35000000000000003,-0.4373076923076924]
[6,29,2018,6,11,9,-0.30000000000000004,-0.30000000000000004,"2018-06-29T06:11:09",-0.35499999999999998,-0.37038461538461537]
[6,29,2018,6,12,9,0,0,"2018-06-29T06:12:09",-0.13,-0.2630769230769231]
[6,29,2018,6,13,9,-0.15000000000000002,-0.15000000000000002,"2018-06-29T06:13:09",-0.10000000000000002,-0.23653846153846153]
[6,29,2018,6,13,39,-0.33,-0.33,"2018-06-29T06:13:39",-0.22,-0.23192307692307684]
[6,29,2018,6,14,39,-0.39,-0.39,"2018-06-29T06:14:39",-0.36000000000000004,-0.23423076923076921]
[6,29,2018,6,15,29,-0.48,-0.48,"2018-06-29T06:15:29",-0.42999999999999994,-0.25153846153846149]
[6,29,2018,6,16,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T06:16:29",-0.44500000000000001,-0.32423076923076927]
[6,29,2018,6,17,19,-0.39,-0.39,"2018-06-29T06:17:19",-0.43,-0.39]
[6,29,2018,6,18,9,-0.42000000000000004,-0.42000000000000004,"2018-06-29T06:18:09",-0.38999999999999996,-0.41423076923076924]
[6,29,2018,6,18,19,-0.44999999999999996,-0.44999999999999996,"2018-06-29T06:18:19",-0.39999999999999991,-0.41884615384615381]
[6,29,2018,6,19,9,-0.33,-0.33,"2018-06-29T06:19:09",-0.40500000000000003,-0.42346153846153844]
[6,29,2018,6,19,59,-0.30000000000000004,-0.30000000000000004,"2018-06-29T06:19:59",-0.315,-0.39346153846153853]
[6,29,2018,6,20,59,-0.21000000000000002,-0.21000000000000002,"2018-06-29T06:20:59",-0.26,-0.35884615384615387]
[6,29,2018,6,21,49,-0.21000000000000002,-0.21000000000000002,"2018-06-29T06:21:49",-0.16500000000000001,-0.30346153846153839]
[6,29,2018,6,22,49,-0.06,-0.06,"2018-06-29T06:22:49",-0.13,-0.23884615384615385]
[6,29,2018,6,23,39,-0.06,-0.06,"2018-06-29T06:23:39",-5.5E-2,-0.17769230769230762]
[6,29,2018,6,24,29,0,0,"2018-06-29T06:24:29",-0.04,-0.12576923076923074]
[6,29,2018,6,25,29,-0.15000000000000002,-0.15000000000000002,"2018-06-29T06:25:29",-9.0000000000000011E-2,-9.1153846153846169E-2]
[6,29,2018,6,26,19,-0.18,-0.18,"2018-06-29T06:26:19",-0.155,-9.0000000000000024E-2]
[6,29,2018,6,27,9,-0.24,-0.24,"2018-06-29T06:27:09",-0.20499999999999999,-0.10846153846153847]
[6,29,2018,6,27,39,-0.21000000000000002,-0.21000000000000002,"2018-06-29T06:27:39",{"$f":"AVERAGE(G7928:G7933)","v":-0.22999999999999998},-0.12923076923076923]
[6,29,2018,6,28,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T06:28:49",-0.22500000000000001,-0.1788461538461539]
[6,29,2018,6,28,59,-0.30000000000000004,-0.30000000000000004,"2018-06-29T06:28:59",-0.24000000000000002,-0.18923076923076926]
[6,29,2018,6,29,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T06:29:49",-0.33000000000000007,-0.23423076923076919]
[6,29,2018,6,30,39,-0.36,-0.36,"2018-06-29T06:30:39",-0.30499999999999999,-0.2630769230769231]
[6,29,2018,6,31,39,-0.44999999999999996,-0.44999999999999996,"2018-06-29T06:31:39",-0.40000000000000008,-0.30576923076923079]
[6,29,2018,6,32,29,-0.44999999999999996,-0.44999999999999996,"2018-06-29T06:32:29",-0.45,-0.35076923076923072]
[6,29,2018,6,33,29,-0.44999999999999996,-0.44999999999999996,"2018-06-29T06:33:29",-0.43,-0.38884615384615384]
[6,29,2018,6,34,19,-0.30000000000000004,-0.30000000000000004,"2018-06-29T06:34:19",-0.36000000000000004,-0.39230769230769236]
[6,29,2018,6,35,9,-0.27,-0.27,"2018-06-29T06:35:09",-0.29500000000000004,-0.38653846153846155]
[6,29,2018,6,36,9,-0.39,-0.39,"2018-06-29T06:36:09",-0.30000000000000004,-0.36115384615384616]
[6,29,2018,6,36,59,-0.15000000000000002,-0.15000000000000002,"2018-06-29T06:36:59",-0.29000000000000004,-0.3265384615384615]
[6,29,2018,6,37,49,-0.44999999999999996,-0.44999999999999996,"2018-06-29T06:37:49",-0.245,-0.29423076923076918]
[6,29,2018,6,38,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T06:38:49",-0.37000000000000005,-0.30115384615384616]
[6,29,2018,6,39,39,-0.21000000000000002,-0.21000000000000002,"2018-06-29T06:39:39",-0.24,-0.29076923076923078]
[6,29,2018,6,39,49,-0.21000000000000002,-0.21000000000000002,"2018-06-29T06:39:49",-0.22499999999999998,-0.28730769230769232]
[6,29,2018,6,40,39,-0.12,-0.12,"2018-06-29T06:40:39",-0.19000000000000003,-0.26192307692307693]
[6,29,2018,6,41,49,-0.09,-0.09,"2018-06-29T06:41:49",-2.4999999999999998E-2,-0.21000000000000002]
[6,29,2018,6,42,19,-0.15000000000000002,-0.15000000000000002,"2018-06-29T06:42:19",-8.5000000000000006E-2,-0.17999999999999997]
[6,29,2018,6,43,9,-0.24,-0.24,"2018-06-29T06:43:09",-0.18999999999999997,-0.14884615384615382]
[6,29,2018,6,43,59,-0.30000000000000004,-0.30000000000000004,"2018-06-29T06:43:59",-0.28500000000000003,-0.16153846153846155]
[6,29,2018,6,44,59,-0.48,-0.48,"2018-06-29T06:44:59",-0.41499999999999998,-0.21346153846153848]
[6,29,2018,6,45,49,-0.66,-0.66,"2018-06-29T06:45:49",-0.56000000000000005,-0.32076923076923081]
[6,29,2018,6,46,49,-0.78,-0.78,"2018-06-29T06:46:49",-0.74500000000000011,-0.46730769230769226]
[6,29,2018,6,47,39,-0.89999999999999991,-0.89999999999999991,"2018-06-29T06:47:39",-0.80500000000000005,-0.58153846153846156]
[6,29,2018,6,48,29,-0.86999999999999988,-0.86999999999999988,"2018-06-29T06:48:29",-0.9049999999999998,-0.69576923076923081]
[6,29,2018,6,49,29,-0.66,-0.66,"2018-06-29T06:49:29",-0.73999999999999988,-0.76500000000000012]
[6,29,2018,6,50,19,-0.39,-0.39,"2018-06-29T06:50:19",-0.53,-0.74423076923076947]
[6,29,2018,6,50,29,-0.33,-0.33,"2018-06-29T06:50:29",-0.47500000000000003,-0.7303846153846153]
[6,29,2018,6,51,19,0.03,0.03,"2018-06-29T06:51:19",-9.5000000000000015E-2,-0.59076923076923082]
[6,29,2018,6,52,9,-0.33,-0.33,"2018-06-29T06:52:09",-0.14500000000000002,-0.46384615384615385]
[6,29,2018,6,53,9,-0.48,-0.48,"2018-06-29T06:53:09",-0.38000000000000006,-0.34961538461538461]
[6,29,2018,6,53,59,-0.48,-0.48,"2018-06-29T06:53:59",-0.49499999999999994,-0.31384615384615383]
[6,29,2018,6,54,49,-0.33,-0.33,"2018-06-29T06:54:49",-0.41,-0.3034615384615385]
[6,29,2018,6,55,59,-0.15000000000000002,-0.15000000000000002,"2018-06-29T06:55:59",-0.215,-0.35538461538461552]
[6,29,2018,6,56,29,-0.03,-0.03,"2018-06-29T06:56:29",-0.13,-0.33000000000000007]
[6,29,2018,6,57,29,0.03,0.03,"2018-06-29T06:57:29",-1.4999999999999999E-2,-0.2457692307692308]
[6,29,2018,6,58,19,-0.12,-0.12,"2018-06-29T06:58:19",-0.03,-0.15807692307692306]
[6,29,2018,6,59,9,-0.27,-0.27,"2018-06-29T06:59:09",-0.18500000000000003,-0.12000000000000002]
[6,29,2018,7,0,9,-0.15000000000000002,-0.15000000000000002,"2018-06-29T07:00:09",-0.22500000000000001,-0.1153846153846154]
[6,29,2018,7,0,59,-0.18,-0.18,"2018-06-29T07:00:59",-0.22499999999999998,-0.14538461538461542]
[6,29,2018,7,1,9,-0.15000000000000002,-0.15000000000000002,"2018-06-29T07:01:09",-0.22500000000000001,-0.15000000000000002]
[6,29,2018,7,1,59,-0.12,-0.12,"2018-06-29T07:01:59",-0.13,-0.17653846153846159]
[6,29,2018,7,2,49,-0.24,-0.24,"2018-06-29T07:02:49",-0.19000000000000003,-0.20076923076923078]
[6,29,2018,7,3,49,-0.06,-0.06,"2018-06-29T07:03:49",-0.19999999999999998,-0.18923076923076926]
[6,29,2018,7,4,39,-0.03,-0.03,"2018-06-29T07:04:39",-2.4999999999999998E-2,-0.15576923076923077]
[6,29,2018,7,5,29,-0.09,-0.09,"2018-06-29T07:05:29",-0.12,-0.13961538461538459]
[6,29,2018,7,6,29,-0.09,-0.09,"2018-06-29T07:06:29",-7.4999999999999997E-2,-0.12692307692307689]
[6,29,2018,7,7,19,-0.30000000000000004,-0.30000000000000004,"2018-06-29T07:07:19",-0.21000000000000005,-0.13038461538461538]
[6,29,2018,7,8,19,-0.09,-0.09,"2018-06-29T07:08:19",-0.13,-0.12115384615384617]
[6,29,2018,7,9,9,-0.21000000000000002,-0.21000000000000002,"2018-06-29T07:09:09",-0.17500000000000002,-0.15000000000000002]
[6,29,2018,7,9,59,-0.27,-0.27,"2018-06-29T07:09:59",-0.26,-0.17769230769230765]
[6,29,2018,7,10,29,-0.30000000000000004,-0.30000000000000004,"2018-06-29T07:10:29",-0.28000000000000003,-0.20423076923076919]
[6,29,2018,7,11,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T07:11:39",-0.28499999999999998,-0.23076923076923081]
[6,29,2018,7,12,29,-0.30000000000000004,-0.30000000000000004,"2018-06-29T07:12:29",-0.34500000000000003,-0.27230769230769231]
[6,29,2018,7,12,39,-0.21000000000000002,-0.21000000000000002,"2018-06-29T07:12:39",-0.32999999999999996,-0.27692307692307694]
[6,29,2018,7,13,29,-0.27,-0.27,"2018-06-29T07:13:29",-0.18000000000000002,-0.27346153846153853]
[6,29,2018,7,14,29,-0.27,-0.27,"2018-06-29T07:14:29",-0.33499999999999996,-0.28846153846153855]
[6,29,2018,7,15,19,-0.51,-0.51,"2018-06-29T07:15:19",-0.35499999999999998,-0.29884615384615387]
[6,29,2018,7,16,9,-0.42000000000000004,-0.42000000000000004,"2018-06-29T07:16:09",-0.48000000000000004,-0.33576923076923076]
[6,29,2018,7,17,9,-0.24,-0.24,"2018-06-29T07:17:09",-0.35499999999999998,-0.34961538461538461]
[6,29,2018,7,17,59,-0.24,-0.24,"2018-06-29T07:17:59",-0.19500000000000003,-0.34384615384615391]
[6,29,2018,7,18,59,-0.12,-0.12,"2018-06-29T07:18:59",-0.16500000000000001,-0.30807692307692314]
[6,29,2018,7,19,49,-0.21000000000000002,-0.21000000000000002,"2018-06-29T07:19:49",-0.105,-0.24461538461538465]
[6,29,2018,7,20,39,-0.36,-0.36,"2018-06-29T07:20:39",-0.31499999999999995,-0.22500000000000009]
[6,29,2018,7,21,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T07:21:39",-0.30499999999999999,-0.22038461538461537]
[6,29,2018,7,22,29,-0.36,-0.36,"2018-06-29T07:22:29",-0.33,-0.24807692307692306]
[6,29,2018,7,23,19,-0.33,-0.33,"2018-06-29T07:23:19",-0.375,-0.2919230769230769]
[6,29,2018,7,23,29,-0.33,-0.33,"2018-06-29T07:23:29",-0.37000000000000005,-0.30692307692307691]
[6,29,2018,7,24,39,-0.33,-0.33,"2018-06-29T07:24:39",-0.32500000000000001,-0.33461538461538459]
[6,29,2018,7,25,9,-0.36,-0.36,"2018-06-29T07:25:09",-0.35000000000000003,-0.33461538461538465]
[6,29,2018,7,25,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T07:25:59",-0.40499999999999997,-0.35653846153846153]
[6,29,2018,7,26,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T07:26:49",-0.45999999999999996,-0.3807692307692308]
[6,29,2018,7,27,49,-0.57000000000000006,-0.57000000000000006,"2018-06-29T07:27:49",-0.55000000000000016,-0.42230769230769233]
[6,29,2018,7,28,39,-0.48,-0.48,"2018-06-29T07:28:39",-0.50000000000000011,-0.45576923076923082]
[6,29,2018,7,29,39,-0.48,-0.48,"2018-06-29T07:29:39",-0.45500000000000002,-0.48115384615384615]
[6,29,2018,7,30,29,-0.51,-0.51,"2018-06-29T07:30:29",-0.47000000000000003,-0.4869230769230769]
[6,29,2018,7,31,19,-0.39,-0.39,"2018-06-29T07:31:19",-0.43500000000000005,-0.47769230769230775]
[6,29,2018,7,32,19,-0.30000000000000004,-0.30000000000000004,"2018-06-29T07:32:19",-0.34999999999999992,-0.42923076923076936]
[6,29,2018,7,33,9,-0.09,-0.09,"2018-06-29T07:33:09",-0.20000000000000004,-0.37384615384615383]
[6,29,2018,7,33,59,-0.21000000000000002,-0.21000000000000002,"2018-06-29T07:33:59",-0.13,-0.31269230769230766]
[6,29,2018,7,34,9,-0.27,-0.27,"2018-06-29T07:34:09",-0.16,-0.30576923076923074]
[6,29,2018,7,34,59,-0.39,-0.39,"2018-06-29T07:34:59",-0.35500000000000004,{"$f":"AVERAGE(G8312:G8337)","v":-0.28384615384615386}]
[6,29,2018,7,35,59,-0.54,-0.54,"2018-06-29T07:35:59",-0.49499999999999994,-0.31269230769230766]
[6,29,2018,7,36,49,-0.54,-0.54,"2018-06-29T07:36:49",-0.55500000000000005,-0.35307692307692307]
[6,29,2018,7,37,39,-0.57000000000000006,-0.57000000000000006,"2018-06-29T07:37:39",-0.56000000000000005,-0.435]
[6,29,2018,7,38,49,-0.54,-0.54,"2018-06-29T07:38:49",-0.56500000000000006,-0.52961538461538471]
[6,29,2018,7,39,19,-0.60000000000000009,-0.60000000000000009,"2018-06-29T07:39:19",-0.56000000000000016,-0.55038461538461536]
[6,29,2018,7,40,9,-0.48,-0.48,"2018-06-29T07:40:09",-0.55500000000000005,-0.56192307692307686]
[6,29,2018,7,41,9,-0.51,-0.51,"2018-06-29T07:41:09",-0.51000000000000012,-0.55153846153846164]
[6,29,2018,7,41,59,-0.54,-0.54,"2018-06-29T07:41:59",-0.53000000000000014,-0.54576923076923078]
[6,29,2018,7,42,59,-0.42000000000000004,-0.42000000000000004,"2018-06-29T07:42:59",-0.48,-0.52269230769230768]
[6,29,2018,7,43,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T07:43:49",-0.44500000000000001,-0.50076923076923074]
[6,29,2018,7,44,39,-0.36,-0.36,"2018-06-29T07:44:39",-0.35999999999999993,-0.4638461538461538]
[6,29,2018,7,44,49,-0.33,-0.33,"2018-06-29T07:44:49",-0.34499999999999997,-0.45807692307692299]
[6,29,2018,7,45,39,-0.36,-0.36,"2018-06-29T07:45:39",-0.38999999999999996,{"$f":"AVERAGE(G8376:G8401)","v":-0.43730769230769223}]
[6,29,2018,7,46,39,-0.51,-0.51,"2018-06-29T07:46:39",-0.43999999999999995,-0.41653846153846152]
[6,29,2018,7,47,29,-0.66,-0.66,"2018-06-29T07:47:29",-0.58000000000000007,-0.44192307692307692]
[6,29,2018,7,48,19,-0.63,-0.63,"2018-06-29T07:48:19",-0.60499999999999998,-0.47423076923076923]
[6,29,2018,7,49,19,-0.57000000000000006,-0.57000000000000006,"2018-06-29T07:49:19",-0.61,-0.53307692307692323]
[6,29,2018,7,50,9,-0.54,-0.54,"2018-06-29T07:50:09",-0.54500000000000004,-0.5607692307692308]
[6,29,2018,7,50,59,-0.51,-0.51,"2018-06-29T07:50:59",-0.52499999999999991,-0.57346153846153847]
[6,29,2018,7,51,59,-0.36,-0.36,"2018-06-29T07:51:59",-0.44500000000000001,-0.53538461538461535]
[6,29,2018,7,52,49,-0.12,-0.12,"2018-06-29T07:52:49",-0.25,-0.4696153846153846]
[6,29,2018,7,53,19,0,0,"2018-06-29T07:53:19",-9.4999999999999987E-2,-0.39807692307692299]
[6,29,2018,7,54,29,-0.09,-0.09,"2018-06-29T07:54:29",-0.02,-0.25615384615384618]
[6,29,2018,7,55,19,-0.21000000000000002,-0.21000000000000002,"2018-06-29T07:55:19",-0.14499999999999999,-0.18576923076923077]
[6,29,2018,7,55,29,-0.21000000000000002,-0.21000000000000002,"2018-06-29T07:55:29",-0.16500000000000001,-0.17423076923076924]
[6,29,2018,7,56,19,-0.42000000000000004,-0.42000000000000004,"2018-06-29T07:56:19",-0.315,{"$f":"AVERAGE(G8440:G8465)","v":-0.1557692307692308}]
[6,29,2018,7,57,9,-0.39,-0.39,"2018-06-29T07:57:09",-0.40000000000000008,-0.18807692307692306]
[6,29,2018,7,58,9,-0.36,-0.36,"2018-06-29T07:58:09",-0.39000000000000007,-0.27576923076923071]
[6,29,2018,7,58,59,-0.33,-0.33,"2018-06-29T07:58:59",-0.34500000000000003,-0.32999999999999996]
[6,29,2018,7,59,59,-0.27,-0.27,"2018-06-29T07:59:59",-0.33499999999999996,-0.36346153846153839]
[6,29,2018,8,0,49,-0.12,-0.12,"2018-06-29T08:00:49",-0.20499999999999999,-0.33000000000000013]
[6,29,2018,8,1,39,-0.18,-0.18,"2018-06-29T08:01:39",-0.155,-0.28615384615384626]
[6,29,2018,8,2,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T08:02:39",-0.23499999999999999,-0.25153846153846154]
[6,29,2018,8,3,29,-0.39,-0.39,"2018-06-29T08:03:29",-0.36000000000000004,-0.25846153846153841]
[6,29,2018,8,4,29,-0.36,-0.36,"2018-06-29T08:04:29",-0.34999999999999992,-0.26538461538461544]
[6,29,2018,8,5,19,-0.27,-0.27,"2018-06-29T08:05:19",-0.33,-0.29653846153846164]
[6,29,2018,8,6,9,-0.21000000000000002,-0.21000000000000002,"2018-06-29T08:06:09",-0.28000000000000003,-0.31500000000000006]
[6,29,2018,8,6,19,-0.21000000000000002,-0.21000000000000002,"2018-06-29T08:06:19",-0.27,-0.31615384615384623]
[6,29,2018,8,7,29,-0.18,-0.18,"2018-06-29T08:07:29",-0.17499999999999996,-0.2838461538461538]
[6,29,2018,8,7,49,-0.18,-0.18,"2018-06-29T08:07:49",-0.17999999999999997,-0.26769230769230762]
[6,29,2018,8,8,49,-0.18,-0.18,"2018-06-29T08:08:49",-0.16500000000000001,-0.22499999999999995]
[6,29,2018,8,9,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T08:09:39",-0.25,-0.21346153846153854]
[6,29,2018,8,10,39,-0.39,-0.39,"2018-06-29T08:10:39",-0.32000000000000006,-0.22500000000000006]
[6,29,2018,8,11,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T08:11:29",-0.41,-0.26999999999999996]
[6,29,2018,8,12,19,-0.12,-0.12,"2018-06-29T08:12:19",-0.23000000000000007,-0.27346153846153848]
[6,29,2018,8,13,19,-0.39,-0.39,"2018-06-29T08:13:19",-0.315,-0.30230769230769233]
[6,29,2018,8,14,9,-0.24,-0.24,"2018-06-29T08:14:09",-0.29499999999999998,-0.30576923076923079]
[6,29,2018,8,15,9,-0.33,-0.33,"2018-06-29T08:15:09",-0.32,-0.30000000000000004]
[6,29,2018,8,15,59,-0.27,-0.27,"2018-06-29T08:15:59",-0.29500000000000004,-0.27576923076923077]
[6,29,2018,8,16,49,-0.36,-0.36,"2018-06-29T08:16:49",-0.29499999999999998,-0.30576923076923085]
[6,29,2018,8,16,59,-0.42000000000000004,-0.42000000000000004,"2018-06-29T08:16:59",-0.32,-0.31384615384615394]
[6,29,2018,8,17,49,-0.39,-0.39,"2018-06-29T08:17:49",-0.42500000000000004,-0.32538461538461549]
[6,29,2018,8,18,39,-0.24,-0.24,"2018-06-29T08:18:39",-0.315,-0.3323076923076923]
[6,29,2018,8,19,39,-0.12,-0.12,"2018-06-29T08:19:39",-0.155,-0.29307692307692312]
[6,29,2018,8,20,29,-0.33,-0.33,"2018-06-29T08:20:29",-0.23500000000000001,-0.28961538461538461]
[6,29,2018,8,21,29,-0.30000000000000004,-0.30000000000000004,"2018-06-29T08:21:29",-0.32,-0.28269230769230769]
[6,29,2018,8,21,59,-0.27,-0.27,"2018-06-29T08:21:59",-0.30000000000000004,-0.26538461538461539]
[6,29,2018,8,22,59,-0.48,-0.48,"2018-06-29T08:22:59",-0.34,-0.27115384615384619]
[6,29,2018,8,23,59,-0.39,-0.39,"2018-06-29T08:23:59",-0.45500000000000002,-0.34038461538461545]
[6,29,2018,8,24,49,-0.36,-0.36,"2018-06-29T08:24:49",-0.34499999999999997,-0.3553846153846153]
[6,29,2018,8,25,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T08:25:39",-0.34999999999999992,-0.36000000000000004]
[6,29,2018,8,26,39,-0.24,-0.24,"2018-06-29T08:26:39",-0.20499999999999999,-0.3438461538461538]
[6,29,2018,8,27,29,-0.33,-0.33,"2018-06-29T08:27:29",-0.33,-0.33]
[6,29,2018,8,27,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T08:27:39",-0.34,-0.32307692307692309]
[6,29,2018,8,28,29,-0.27,-0.27,"2018-06-29T08:28:29",-0.255,-0.29192307692307701]
[6,29,2018,8,29,19,-0.24,-0.24,"2018-06-29T08:29:19",-0.29500000000000004,-0.28384615384615386]
[6,29,2018,8,30,19,-0.12,-0.12,"2018-06-29T08:30:19",-0.19000000000000003,-0.25730769230769235]
[6,29,2018,8,31,9,-0.18,-0.18,"2018-06-29T08:31:09",-0.14000000000000001,-0.24230769230769236]
[6,29,2018,8,32,9,-0.21000000000000002,-0.21000000000000002,"2018-06-29T08:32:09",-0.22999999999999998,-0.22038461538461543]
[6,29,2018,8,32,59,-0.36,-0.36,"2018-06-29T08:32:59",-0.26,-0.2215384615384616]
[6,29,2018,8,33,49,-0.48,-0.48,"2018-06-29T08:33:49",-0.48000000000000004,-0.26423076923076927]
[6,29,2018,8,34,49,-0.51,-0.51,"2018-06-29T08:34:49",-0.46999999999999992,-0.33346153846153848]
[6,29,2018,8,35,39,-0.44999999999999996,-0.44999999999999996,"2018-06-29T08:35:39",{"$f":"AVERAGE(G8696:G8701)","v":-0.48},-0.39461538461538459]
[6,29,2018,8,36,9,-0.44999999999999996,-0.44999999999999996,"2018-06-29T08:36:09",-0.46500000000000002,-0.42115384615384605]
[6,29,2018,8,37,19,-0.42000000000000004,-0.42000000000000004,"2018-06-29T08:37:19",-0.45,-0.47192307692307689]
[6,29,2018,8,38,9,-0.44999999999999996,-0.44999999999999996,"2018-06-29T08:38:09",-0.47499999999999992,-0.46846153846153843]
[6,29,2018,8,38,19,-0.42000000000000004,-0.42000000000000004,"2018-06-29T08:38:19",-0.47499999999999992,-0.46846153846153843]
[6,29,2018,8,39,9,-0.39,-0.39,"2018-06-29T08:39:09",-0.44999999999999996,-0.4638461538461538]
[6,29,2018,8,39,59,-0.24,-0.24,"2018-06-29T08:39:59",-0.31,-0.42923076923076925]
[6,29,2018,8,40,59,-0.30000000000000004,-0.30000000000000004,"2018-06-29T08:40:59",-0.3,-0.38538461538461538]
[6,29,2018,8,41,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T08:41:49",-0.39500000000000002,-0.38307692307692309]
[6,29,2018,8,42,49,-0.57000000000000006,-0.57000000000000006,"2018-06-29T08:42:49",-0.52500000000000002,-0.39692307692307693]
[6,29,2018,8,43,39,-0.51,-0.51,"2018-06-29T08:43:39",-0.52,-0.41076923076923078]
[6,29,2018,8,44,29,-0.27,-0.27,"2018-06-29T08:44:29",-0.39000000000000007,-0.42923076923076919]
[6,29,2018,8,45,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T08:45:29",-0.48500000000000004,-0.46730769230769237]
[6,29,2018,8,46,19,-0.48,-0.48,"2018-06-29T08:46:19",{"$f":"AVERAGE(G8760:G8765)","v":-0.49},-0.47999999999999993]
[6,29,2018,8,47,9,-0.66,-0.66,"2018-06-29T08:47:09",-0.58500000000000008,-0.48807692307692296]
[6,29,2018,8,48,9,-0.51,-0.51,"2018-06-29T08:48:09",-0.60499999999999998,-0.51346153846153841]
[6,29,2018,8,48,59,-0.36,-0.36,"2018-06-29T08:48:59",-0.44999999999999996,-0.53192307692307683]
[6,29,2018,8,49,9,-0.36,-0.36,"2018-06-29T08:49:09",-0.42499999999999999,-0.52730769230769226]
[6,29,2018,8,50,19,-0.27,-0.27,"2018-06-29T08:50:19",-0.22,-0.45346153846153858]
[6,29,2018,8,50,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T08:50:39",-0.25000000000000006,-0.43846153846153862]
[6,29,2018,8,51,39,-0.39,-0.39,"2018-06-29T08:51:39",-0.35000000000000003,-0.37615384615384617]
[6,29,2018,8,52,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T08:52:29",-0.43,-0.34730769230769226]
[6,29,2018,8,53,19,-0.24,-0.24,"2018-06-29T08:53:19",-0.33499999999999996,-0.32423076923076921]
[6,29,2018,8,54,19,-0.24,-0.24,"2018-06-29T08:54:19",-0.19999999999999998,-0.31384615384615383]
[6,29,2018,8,55,9,-0.42000000000000004,-0.42000000000000004,"2018-06-29T08:55:09",-0.31,-0.32307692307692304]
[6,29,2018,8,56,9,-0.30000000000000004,-0.30000000000000004,"2018-06-29T08:56:09",-0.32,-0.31269230769230766]
[6,29,2018,8,56,59,-0.18,-0.18,"2018-06-29T08:56:59",{"$f":"AVERAGE(G8824:G8829)","v":-0.21999999999999997},-0.26769230769230762]
[6,29,2018,8,57,49,-0.27,-0.27,"2018-06-29T08:57:49",-0.19999999999999998,-0.25384615384615378]
[6,29,2018,8,58,49,-0.39,-0.39,"2018-06-29T08:58:49",-0.35000000000000009,-0.28499999999999992]
[6,29,2018,8,59,39,-0.36,-0.36,"2018-06-29T08:59:39",-0.34500000000000003,-0.28384615384615391]
[6,29,2018,8,59,49,-0.36,-0.36,"2018-06-29T08:59:49",-0.34,-0.28269230769230774]
[6,29,2018,9,0,39,-0.33,-0.33,"2018-06-29T09:00:39",-0.35499999999999998,-0.29538461538461547]
[6,29,2018,9,1,29,-0.27,-0.27,"2018-06-29T09:01:29",-0.28499999999999998,-0.31269230769230771]
[6,29,2018,9,2,29,-0.21000000000000002,-0.21000000000000002,"2018-06-29T09:02:29",-0.245,-0.31269230769230771]
[6,29,2018,9,3,19,-0.24,-0.24,"2018-06-29T09:03:19",-0.24,-0.29076923076923078]
[6,29,2018,9,4,9,-0.24,-0.24,"2018-06-29T09:04:09",-0.28000000000000003,-0.2803846153846154]
[6,29,2018,9,4,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T09:04:49",-0.26,-0.26538461538461539]
[6,29,2018,9,5,49,-0.33,-0.33,"2018-06-29T09:05:49",-0.33,-0.27576923076923082]
[6,29,2018,9,6,49,-0.15000000000000002,-0.15000000000000002,"2018-06-29T09:06:49",-0.24500000000000002,-0.27576923076923082]
[6,29,2018,9,7,39,-0.24,-0.24,"2018-06-29T09:07:39",{"$f":"AVERAGE(G8888:G8893)","v":-0.18000000000000002},-0.26423076923076927]
[6,29,2018,9,8,29,-0.24,-0.24,"2018-06-29T09:08:29",-0.21,-0.24807692307692311]
[6,29,2018,9,9,29,-0.30000000000000004,-0.30000000000000004,"2018-06-29T09:09:29",-0.26500000000000001,-0.24576923076923077]
[6,29,2018,9,10,19,-0.48,-0.48,"2018-06-29T09:10:19",-0.42500000000000004,-0.2665384615384615]
[6,29,2018,9,11,9,-0.54,-0.54,"2018-06-29T09:11:09",-0.54,-0.3288461538461539]
[6,29,2018,9,11,19,-0.48,-0.48,"2018-06-29T09:11:19",-0.54,-0.34153846153846162]
[6,29,2018,9,12,9,-0.30000000000000004,-0.30000000000000004,"2018-06-29T09:12:09",-0.40499999999999997,-0.37846153846153852]
[6,29,2018,9,13,9,-0.30000000000000004,-0.30000000000000004,"2018-06-29T09:13:09",-0.32,-0.40269230769230785]
[6,29,2018,9,13,59,-0.33,-0.33,"2018-06-29T09:13:59",-0.25,-0.39115384615384613]
[6,29,2018,9,14,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T09:14:49",-0.23500000000000001,-0.34153846153846157]
[6,29,2018,9,15,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T09:15:49",-0.5,-0.33692307692307694]
[6,29,2018,9,16,39,-0.57000000000000006,-0.57000000000000006,"2018-06-29T09:16:39",-0.40500000000000003,-0.34269230769230768]
[6,29,2018,9,17,39,-0.12,-0.12,{"$f":"DATE(C8953,A8953,B8953)+TIME(D8953,E8953,F8953)","v":"2018-06-29T09:17:39"},-0.17,-0.31038461538461537]
[6,29,2018,9,18,29,-0.12,-0.12,"2018-06-29T09:18:29",-0.14000000000000001,-0.29192307692307701]
[6,29,2018,9,18,59,-0.18,-0.18,"2018-06-29T09:18:59",-0.155,-0.29538461538461547]
[6,29,2018,9,20,9,-0.33,-0.33,"2018-06-29T09:20:09",-0.22,-0.218076923076923]
[6,29,2018,9,20,59,-0.36,-0.36,"2018-06-29T09:20:59",-0.38999999999999996,-0.21807692307692311]
[6,29,2018,9,21,49,-0.27,-0.27,"2018-06-29T09:21:49",-0.32,-0.24346153846153845]
[6,29,2018,9,21,59,-0.24,-0.24,"2018-06-29T09:21:59",-0.3,-0.24807692307692311]
[6,29,2018,9,22,49,-0.33,-0.33,"2018-06-29T09:22:49",-0.26000000000000006,-0.27115384615384619]
[6,29,2018,9,23,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T09:23:49",-0.33000000000000007,-0.31615384615384617]
[6,29,2018,9,24,39,-0.39,-0.39,"2018-06-29T09:24:39",-0.40500000000000003,-0.33692307692307699]
[6,29,2018,9,25,29,-0.33,-0.33,"2018-06-29T09:25:29",-0.36500000000000005,-0.33]
[6,29,2018,9,26,29,-0.21000000000000002,-0.21000000000000002,"2018-06-29T09:26:29",-0.27499999999999997,-0.33115384615384624]
[6,29,2018,9,27,19,-0.06,-0.06,"2018-06-29T09:27:19",-9.5000000000000015E-2,-0.28846153846153844]
[6,29,2018,9,28,19,-0.06,-0.06,{"$f":"DATE(C9017,A9017,B9017)+TIME(D9017,E9017,F9017)","v":"2018-06-29T09:28:19"},-8.5000000000000006E-2,-0.23076923076923073]
[6,29,2018,9,29,9,0,0,"2018-06-29T09:29:09",5.0000000000000001E-3,-0.14769230769230768]
[6,29,2018,9,29,59,-0.09,-0.09,"2018-06-29T09:29:59",-7.4999999999999997E-2,-9.6923076923076903E-2]
[6,29,2018,9,30,59,-0.15000000000000002,-0.15000000000000002,"2018-06-29T09:30:59",-9.9999999999999992E-2,-6.4615384615384644E-2]
[6,29,2018,9,31,49,-0.24,-0.24,"2018-06-29T09:31:49",-0.20000000000000004,-0.09]
[6,29,2018,9,32,39,-0.21000000000000002,-0.21000000000000002,"2018-06-29T09:32:39",-0.18999999999999997,-0.11192307692307693]
[6,29,2018,9,32,49,-0.15000000000000002,-0.15000000000000002,"2018-06-29T09:32:49",-0.17500000000000004,-0.11653846153846154]
[6,29,2018,9,34,9,-0.03,-0.03,"2018-06-29T09:34:09",-0.06,-0.13499999999999998]
[6,29,2018,9,34,29,0.03,0.03,"2018-06-29T09:34:29",-0.04,-0.12692307692307689]
[6,29,2018,9,35,19,0,0,"2018-06-29T09:35:19",-0.01,-0.11192307692307688]
[6,29,2018,9,36,9,-0.12,-0.12,"2018-06-29T09:36:09",-9.9999999999999992E-2,-9.4615384615384643E-2]
[6,29,2018,9,37,9,0,0,"2018-06-29T09:37:09",-9.5000000000000015E-2,-7.6153846153846183E-2]
[6,29,2018,9,37,59,-0.06,-0.06,"2018-06-29T09:37:59",-3.4999999999999996E-2,-6.0000000000000012E-2]
[6,29,2018,9,38,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T09:38:49",-0.14500000000000002,-8.7692307692307708E-2]
[6,29,2018,9,39,49,-0.27,-0.27,"2018-06-29T09:39:49",-0.18499999999999997,-0.12346153846153848]
[6,29,2018,9,40,39,-0.27,-0.27,"2018-06-29T09:40:39",-0.26500000000000007,-0.15115384615384617]
[6,29,2018,9,41,39,-0.63,-0.63,"2018-06-29T09:41:39",-0.35499999999999998,-0.21576923076923077]
[6,29,2018,9,42,29,-0.54,-0.54,"2018-06-29T09:42:29",-0.52999999999999992,-0.30346153846153845]
[6,29,2018,9,43,19,-0.66,-0.66,"2018-06-29T09:43:19",-0.52500000000000002,-0.36346153846153845]
[6,29,2018,9,43,29,-0.84000000000000008,-0.84000000000000008,"2018-06-29T09:43:29",-0.57500000000000007,-0.38653846153846155]
[6,29,2018,9,44,19,-0.66,-0.66,"2018-06-29T09:44:19",-0.70500000000000007,-0.48807692307692307]
[6,29,2018,9,45,19,-0.60000000000000009,-0.60000000000000009,"2018-06-29T09:45:19",-0.62500000000000011,-0.57461538461538464]
[6,29,2018,9,46,9,-0.66,-0.66,"2018-06-29T09:46:09",-0.64500000000000002,-0.61153846153846159]
[6,29,2018,9,46,59,-0.66,-0.66,"2018-06-29T09:46:59",-0.63,-0.63461538461538458]
[6,29,2018,9,47,39,-0.75,-0.75,"2018-06-29T09:47:39",-0.66499999999999992,-0.65884615384615397]
[6,29,2018,9,48,39,-0.36,-0.36,"2018-06-29T09:48:39",-0.505,-0.61269230769230776]
[6,29,2018,9,49,29,-0.24,-0.24,"2018-06-29T09:49:29",-0.34999999999999992,-0.55846153846153856]
[6,29,2018,9,50,29,-0.24,-0.24,"2018-06-29T09:50:29",-0.21,-0.4580769230769231]
[6,29,2018,9,51,19,-0.36,-0.36,"2018-06-29T09:51:19",-0.24500000000000002,-0.38538461538461544]
[6,29,2018,9,52,19,-0.60000000000000009,-0.60000000000000009,"2018-06-29T09:52:19",-0.54,-0.35884615384615387]
[6,29,2018,9,53,9,-0.66,-0.66,"2018-06-29T09:53:09",-0.62500000000000011,-0.39576923076923076]
[6,29,2018,9,53,59,-0.84000000000000008,-0.84000000000000008,"2018-06-29T09:53:59",-0.875,-0.51115384615384607]
[6,29,2018,9,54,9,-0.78,-0.78,"2018-06-29T09:54:09",-0.89500000000000002,-0.53423076923076918]
[6,29,2018,9,54,59,-0.69000000000000006,-0.69000000000000006,"2018-06-29T09:54:59",-0.76500000000000001,-0.63576923076923064]
[6,29,2018,9,55,49,-0.54,-0.54,"2018-06-29T09:55:49",-0.55500000000000005,-0.68538461538461537]
[6,29,2018,9,56,49,-0.48,-0.48,"2018-06-29T09:56:49",-0.51,-0.67038461538461547]
[6,29,2018,9,57,39,-0.63,-0.63,"2018-06-29T09:57:39",-0.51500000000000001,-0.64269230769230756]
[6,29,2018,9,58,39,-0.84000000000000008,-0.84000000000000008,"2018-06-29T09:58:39",-0.72500000000000009,-0.60461538461538467]
[6,29,2018,9,59,29,-0.51,-0.51,"2018-06-29T09:59:29",-0.69000000000000006,-0.58846153846153837]
[6,29,2018,10,0,19,-0.30000000000000004,-0.30000000000000004,{"$f":"DATE(C9209,A9209,B9209)+TIME(D9209,E9209,F9209)","v":"2018-06-29T10:00:19"},-0.42499999999999999,-0.5723076923076923]
[6,29,2018,10,1,19,0.06,0.06,"2018-06-29T10:01:19",-3.0000000000000002E-2,-0.46153846153846156]
[6,29,2018,10,1,49,-0.06,-0.06,"2018-06-29T10:01:49",0.01,-0.4096153846153846]
[6,29,2018,10,2,59,-0.12,-0.12,"2018-06-29T10:02:59",-0.105,-0.2446153846153846]
[6,29,2018,10,3,49,-0.09,-0.09,"2018-06-29T10:03:49",-0.08,-0.13153846153846155]
[6,29,2018,10,4,39,0.06,0.06,"2018-06-29T10:04:39",-4.4999999999999991E-2,-6.0000000000000019E-2]
[6,29,2018,10,4,49,-0.15000000000000002,-0.15000000000000002,"2018-06-29T10:04:49",-5.5E-2,-5.8846153846153854E-2]
[6,29,2018,10,5,39,-0.18,-0.18,"2018-06-29T10:05:39",-0.12,-8.0769230769230788E-2]
[6,29,2018,10,6,29,-0.06,-0.06,"2018-06-29T10:06:29",-0.125,-9.0000000000000024E-2]
[6,29,2018,10,7,29,0.24,0.24,"2018-06-29T10:07:29",0.15,-3.1153846153846174E-2]
[6,29,2018,10,8,19,0.09,0.09,"2018-06-29T10:08:19",0.11499999999999998,-1.153846153846172E-3]
[6,29,2018,10,9,19,0.18,0.18,"2018-06-29T10:09:19",0.17499999999999996,4.8461538461538452E-2]
[6,29,2018,10,10,9,0.21000000000000002,0.21000000000000002,"2018-06-29T10:10:09",0.20499999999999999,0.11423076923076922]
[6,29,2018,10,10,59,0.15000000000000002,0.15000000000000002,{"$f":"DATE(C9273,A9273,B9273)+TIME(D9273,E9273,F9273)","v":"2018-06-29T10:10:59"},0.19499999999999998,0.1684615384615385]
[6,29,2018,10,11,59,-0.12,-0.12,"2018-06-29T10:11:59",2.0000000000000007E-2,0.13615384615384613]
[6,29,2018,10,12,49,-0.57000000000000006,-0.57000000000000006,"2018-06-29T10:12:49",-0.32,4.6153846153846115E-2]
[6,29,2018,10,13,49,-1.02,-1.02,"2018-06-29T10:13:49",-0.73,-0.16384615384615386]
[6,29,2018,10,14,39,-1.1099999999999999,-1.1099999999999999,"2018-06-29T10:14:39",-1.0350000000000001,-0.40384615384615385]
[6,29,2018,10,15,29,-1.02,-1.02,"2018-06-29T10:15:29",-1.04,-0.6346153846153848]
[6,29,2018,10,15,39,-0.96,-0.96,"2018-06-29T10:15:39",-1.0149999999999999,-0.67384615384615398]
[6,29,2018,10,16,59,-0.60000000000000009,-0.60000000000000009,"2018-06-29T10:16:59",-0.80999999999999994,-0.88384615384615373]
[6,29,2018,10,17,9,-0.63,-0.63,"2018-06-29T10:17:09",-0.77499999999999991,-0.88615384615384596]
[6,29,2018,10,18,9,-0.18,-0.18,"2018-06-29T10:18:09",-0.33500000000000002,-0.79499999999999982]
[6,29,2018,10,18,59,0.06,0.06,"2018-06-29T10:18:59",-3.5000000000000003E-2,-0.59653846153846157]
[6,29,2018,10,19,59,-0.06,-0.06,"2018-06-29T10:19:59",0,-0.36230769230769239]
[6,29,2018,10,20,49,0,0,"2018-06-29T10:20:49",-6.0000000000000005E-2,-0.20076923076923076]
[6,29,2018,10,21,39,-0.21000000000000002,-0.21000000000000002,{"$f":"DATE(C9337,A9337,B9337)+TIME(D9337,E9337,F9337)","v":"2018-06-29T10:21:39"},-0.13500000000000001,-0.10269230769230769]
[6,29,2018,10,22,39,-0.39,-0.39,"2018-06-29T10:22:39",-0.28000000000000003,-0.105]
[6,29,2018,10,23,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T10:23:29",-0.42,-0.18923076923076926]
[6,29,2018,10,24,19,-0.48,-0.48,"2018-06-29T10:24:19",-0.435,-0.27346153846153853]
[6,29,2018,10,25,19,-0.36,-0.36,"2018-06-29T10:25:19",-0.37000000000000005,-0.34269230769230774]
[6,29,2018,10,26,9,-0.39,-0.39,"2018-06-29T10:26:09",-0.34,-0.37153846153846154]
[6,29,2018,10,26,19,-0.33,-0.33,"2018-06-29T10:26:19",-0.33500000000000002,-0.375]
[6,29,2018,10,27,9,-0.39,-0.39,"2018-06-29T10:27:09",-0.38000000000000006,-0.38884615384615384]
[6,29,2018,10,27,59,-0.60000000000000009,-0.60000000000000009,"2018-06-29T10:27:59",-0.54000000000000015,-0.41884615384615392]
[6,29,2018,10,28,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T10:28:59",-0.48,-0.42461538461538467]
[6,29,2018,10,29,49,-0.24,-0.24,"2018-06-29T10:29:49",-0.41,-0.43730769230769234]
[6,29,2018,10,30,29,-0.44999999999999996,-0.44999999999999996,"2018-06-29T10:30:29",-0.35000000000000009,-0.44423076923076921]
[6,29,2018,10,31,29,-0.09,-0.09,"2018-06-29T10:31:29",-0.17,-0.39576923076923082]
[6,29,2018,10,32,19,0.09,0.09,{"$f":"DATE(C9401,A9401,B9401)+TIME(D9401,E9401,F9401)","v":"2018-06-29T10:32:19"},-1.4999999999999999E-2,-0.2861538461538462]
[6,29,2018,10,33,19,-0.03,-0.03,"2018-06-29T10:33:19",-0.02,-0.18]
[6,29,2018,10,34,9,-0.12,-0.12,"2018-06-29T10:34:09",-0.125,-0.1303846153846154]
[6,29,2018,10,34,59,-0.24,-0.24,"2018-06-29T10:34:59",-0.17500000000000002,-0.10153846153846152]
[6,29,2018,10,35,59,-0.42000000000000004,-0.42000000000000004,"2018-06-29T10:35:59",-0.39999999999999997,-0.16038461538461538]
[6,29,2018,10,36,49,-0.09,-0.09,"2018-06-29T10:36:49",-0.29000000000000004,-0.20884615384615385]
[6,29,2018,10,36,59,-0.09,-0.09,"2018-06-29T10:36:59",-0.23500000000000001,-0.20999999999999996]
[6,29,2018,10,37,49,-0.21000000000000002,-0.21000000000000002,"2018-06-29T10:37:49",-0.125,-0.22846153846153844]
[6,29,2018,10,38,39,-0.12,-0.12,"2018-06-29T10:38:39",-0.16,-0.23076923076923078]
[6,29,2018,10,39,39,-0.39,-0.39,"2018-06-29T10:39:39",-0.29499999999999998,-0.24461538461538457]
[6,29,2018,10,40,29,-0.30000000000000004,-0.30000000000000004,"2018-06-29T10:40:29",-0.30000000000000004,-0.21576923076923074]
[6,29,2018,10,41,29,-0.21000000000000002,-0.21000000000000002,"2018-06-29T10:41:29",-0.19999999999999998,-0.22038461538461543]
[6,29,2018,10,42,19,-0.24,-0.24,"2018-06-29T10:42:19",-0.215,-0.22961538461538461]
[6,29,2018,10,43,9,-0.33,-0.33,"2018-06-29T10:43:09",-0.28500000000000003,-0.25730769230769235]
[6,29,2018,10,44,9,-0.36,-0.36,"2018-06-29T10:44:09",-0.35499999999999998,-0.2688461538461539]
[6,29,2018,10,44,59,-0.39,-0.39,"2018-06-29T10:44:59",-0.43,-0.30230769230769228]
[6,29,2018,10,45,39,-0.44999999999999996,-0.44999999999999996,"2018-06-29T10:45:39",-0.43999999999999995,-0.34499999999999997]
[6,29,2018,10,46,39,-0.36,-0.36,"2018-06-29T10:46:39",-0.41000000000000009,-0.39]
[6,29,2018,10,47,29,-0.39,-0.39,"2018-06-29T10:47:29",-0.31,-0.39115384615384624]
[6,29,2018,10,47,39,-0.18,-0.18,"2018-06-29T10:47:39",-0.27999999999999997,-0.38423076923076926]
[6,29,2018,10,48,29,-0.03,-0.03,"2018-06-29T10:48:29",0,-0.30923076923076925]
[6,29,2018,10,49,19,0,0,"2018-06-29T10:49:19",-0.01,-0.22500000000000009]
[6,29,2018,10,50,19,-0.03,-0.03,"2018-06-29T10:50:19",-0.04,-0.1246153846153846]
[6,29,2018,10,51,9,-0.18,-0.18,"2018-06-29T10:51:09",-0.10999999999999999,-8.1923076923076932E-2]
[6,29,2018,10,51,59,-0.27,-0.27,"2018-06-29T10:51:59",-0.215,-7.0384615384615393E-2]
[6,29,2018,10,52,59,-0.30000000000000004,-0.30000000000000004,"2018-06-29T10:52:59",-0.29500000000000004,-0.14538461538461539]
[6,29,2018,10,53,49,-0.18,-0.18,"2018-06-29T10:53:49",-0.25,-0.18692307692307697]
[6,29,2018,10,54,49,0.21000000000000002,0.21000000000000002,"2018-06-29T10:54:49",-4.5000000000000005E-2,-0.18807692307692309]
[6,29,2018,10,55,39,0.27,0.27,"2018-06-29T10:55:39",0.29499999999999998,-9.6923076923076917E-2]
[6,29,2018,10,56,29,0.24,0.24,"2018-06-29T10:56:29",0.26499999999999996,-3.4615384615384881E-3]
[6,29,2018,10,57,29,0,0,"2018-06-29T10:57:29",0.08,8.4230769230769234E-2]
[6,29,2018,10,58,19,-0.30000000000000004,-0.30000000000000004,"2018-06-29T10:58:19",-0.13,9.4615384615384615E-2]
[6,29,2018,10,58,29,-0.30000000000000004,-0.30000000000000004,"2018-06-29T10:58:29",-0.18000000000000002,8.6538461538461578E-2]
[6,29,2018,10,59,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T10:59:49",-0.41,-8.7692307692307708E-2]
[6,29,2018,10,59,59,-0.54,-0.54,"2018-06-29T10:59:59",-0.435,-0.11884615384615385]
[6,29,2018,11,0,59,-0.39,-0.39,"2018-06-29T11:00:59",-0.45500000000000002,-0.28269230769230769]
[6,29,2018,11,1,49,-0.12,-0.12,"2018-06-29T11:01:49",-0.22999999999999998,-0.33115384615384613]
[6,29,2018,11,2,39,-0.21000000000000002,-0.21000000000000002,"2018-06-29T11:02:39",-0.17500000000000002,-0.33692307692307699]
[6,29,2018,11,3,39,-0.39,-0.39,"2018-06-29T11:03:39",-0.33,-0.32423076923076938]
[6,29,2018,11,4,29,-0.33,-0.33,"2018-06-29T11:04:29",-0.40500000000000003,-0.315]
[6,29,2018,11,5,29,-0.03,-0.03,"2018-06-29T11:05:29",-1.5000000000000005E-2,-0.21923076923076928]
[6,29,2018,11,6,19,-0.33,-0.33,"2018-06-29T11:06:19",-0.25500000000000006,-0.24576923076923082]
[6,29,2018,11,7,9,-0.48,-0.48,"2018-06-29T11:07:09",-0.47500000000000003,-0.3000000000000001]
[6,29,2018,11,8,9,-0.60000000000000009,-0.60000000000000009,"2018-06-29T11:08:09",-0.56500000000000006,-0.34961538461538466]
[6,29,2018,11,8,59,-0.30000000000000004,-0.30000000000000004,"2018-06-29T11:08:59",-0.46500000000000002,-0.36692307692307696]
[6,29,2018,11,9,49,-0.18,-0.18,"2018-06-29T11:09:49",-0.24,-0.41307692307692317]
[6,29,2018,11,9,59,-0.15000000000000002,-0.15000000000000002,"2018-06-29T11:09:59",-0.215,-0.41423076923076935]
[6,29,2018,11,10,49,-0.06,-0.06,"2018-06-29T11:10:49",-0.14500000000000002,-0.37038461538461548]
[6,29,2018,11,11,49,0.09,0.09,"2018-06-29T11:11:49",5.000000000000001E-2,-0.24000000000000002]
[6,29,2018,11,12,39,-0.09,-0.09,"2018-06-29T11:12:39",-0.04,-0.1384615384615385]
[6,29,2018,11,13,19,-0.36,-0.36,"2018-06-29T11:13:19",-0.23500000000000001,-0.1257692307692308]
[6,29,2018,11,14,19,-0.18,-0.18,"2018-06-29T11:14:19",-0.31,-0.14769230769230771]
[6,29,2018,11,15,9,-0.21000000000000002,-0.21000000000000002,"2018-06-29T11:15:09",-0.17,-0.15230769230769231]
[6,29,2018,11,16,9,0,0,"2018-06-29T11:16:09",-0.11,-0.18923076923076926]
[6,29,2018,11,16,59,-0.09,-0.09,"2018-06-29T11:16:59",-0.06,-0.19038461538461543]
[6,29,2018,11,17,49,-0.44999999999999996,-0.44999999999999996,"2018-06-29T11:17:49",-0.255,-0.18115384615384617]
[6,29,2018,11,18,49,-0.03,-0.03,"2018-06-29T11:18:49",-0.21,-0.1684615384615385]
[6,29,2018,11,19,39,0.06,0.06,"2018-06-29T11:19:39",-4.0000000000000008E-2,-0.14423076923076919]
[6,29,2018,11,20,29,-0.21000000000000002,-0.21000000000000002,"2018-06-29T11:20:29",-5.000000000000001E-2,-0.13961538461538459]
[6,29,2018,11,20,39,-0.33,-0.33,"2018-06-29T11:20:39",-0.11499999999999999,-0.15230769230769228]
[6,29,2018,11,21,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T11:21:29",-0.41,-0.21576923076923071]
[6,29,2018,11,22,29,-0.33,-0.33,"2018-06-29T11:22:29",-0.40000000000000008,-0.22615384615384618]
[6,29,2018,11,23,19,-0.36,-0.36,"2018-06-29T11:23:19",-0.46,-0.29884615384615387]
[6,29,2018,11,24,9,-0.18,-0.18,"2018-06-29T11:24:09",-0.31999999999999995,-0.35307692307692312]
[6,29,2018,11,25,9,-0.06,-0.06,"2018-06-29T11:25:09",-0.17,-0.35307692307692329]
[6,29,2018,11,25,59,0.09,0.09,"2018-06-29T11:25:59",-1.0000000000000004E-2,-0.26769230769230773]
[6,29,2018,11,26,59,-0.12,-0.12,"2018-06-29T11:26:59",-6.5000000000000002E-2,-0.1915384615384616]
[6,29,2018,11,27,49,-0.15000000000000002,-0.15000000000000002,"2018-06-29T11:27:49",-0.16500000000000001,-0.13499999999999998]
[6,29,2018,11,28,29,-0.30000000000000004,-0.30000000000000004,"2018-06-29T11:28:29",-0.22500000000000001,-0.12346153846153846]
[6,29,2018,11,29,29,-0.44999999999999996,-0.44999999999999996,"2018-06-29T11:29:29",-0.43,-0.1834615384615384]
[6,29,2018,11,30,19,-0.60000000000000009,-0.60000000000000009,"2018-06-29T11:30:19",-0.55999999999999994,-0.29538461538461536]
[6,29,2018,11,31,9,-0.18,-0.18,"2018-06-29T11:31:09",-0.375,-0.34846153846153849]
[6,29,2018,11,31,19,0.15000000000000002,0.15000000000000002,"2018-06-29T11:31:19",-0.25,-0.33807692307692311]
[6,29,2018,11,32,9,-0.12,-0.12,"2018-06-29T11:32:09",5.5000000000000014E-2,-0.2976923076923077]
[6,29,2018,11,33,9,-0.27,-0.27,"2018-06-29T11:33:09",-0.34,-0.31038461538461537]
[6,29,2018,11,33,59,-0.15000000000000002,-0.15000000000000002,"2018-06-29T11:33:59",-0.16,-0.246923076923077]
[6,29,2018,11,34,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T11:34:49",-0.25,-0.19153846153846155]
[6,29,2018,11,35,49,-0.66,-0.66,"2018-06-29T11:35:49",-0.51000000000000012,-0.27461538461538465]
[6,29,2018,11,36,39,-0.51,-0.51,"2018-06-29T11:36:39",-0.59500000000000008,-0.37730769230769234]
[6,29,2018,11,37,29,-0.27,-0.27,"2018-06-29T11:37:29",-0.36000000000000004,-0.3715384615384616]
[6,29,2018,11,38,29,-0.27,-0.27,"2018-06-29T11:38:29",-0.27500000000000002,-0.40269230769230763]
[6,29,2018,11,39,19,-0.42000000000000004,-0.42000000000000004,"2018-06-29T11:39:19",-0.32000000000000006,-0.40269230769230763]
[6,29,2018,11,40,19,-0.36,-0.36,"2018-06-29T11:40:19",-0.40500000000000003,{"$f":"AVERAGE(G9784:G9809)","v":-0.36923076923076931}]
[6,29,2018,11,41,9,-0.48,-0.48,"2018-06-29T11:41:09",-0.35000000000000003,-0.33576923076923088]
[6,29,2018,11,41,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T11:41:59",-0.51000000000000012,-0.37615384615384617]
[6,29,2018,11,42,39,-0.33,-0.33,"2018-06-29T11:42:39",-0.42500000000000004,-0.39]
[6,29,2018,11,42,49,-0.33,-0.33,"2018-06-29T11:42:49",-0.375,-0.39230769230769236]
[6,29,2018,11,43,49,0.06,0.06,"2018-06-29T11:43:49",-0.20000000000000004,-0.35884615384615387]
[6,29,2018,11,44,39,-0.21000000000000002,-0.21000000000000002,"2018-06-29T11:44:39",-9.0000000000000011E-2,-0.30461538461538468]
[6,29,2018,11,45,29,-0.09,-0.09,"2018-06-29T11:45:29",-0.155,-0.26538461538461539]
[6,29,2018,11,46,29,0.03,0.03,"2018-06-29T11:46:29",8.5000000000000006E-2,-0.12923076923076923]
[6,29,2018,11,47,19,-0.03,-0.03,"2018-06-29T11:47:19",4.5000000000000005E-2,-5.1923076923076891E-2]
[6,29,2018,11,48,9,-0.30000000000000004,-0.30000000000000004,"2018-06-29T11:48:09",-5.000000000000001E-2,-3.2307692307692308E-2]
[6,29,2018,11,49,9,0.18,0.18,"2018-06-29T11:49:09",-0.15000000000000005,-3.692307692307694E-2]
[6,29,2018,11,49,59,-0.24,-0.24,"2018-06-29T11:49:59",-0.04,-3.4615384615384617E-2]
[6,29,2018,11,50,59,-0.42000000000000004,-0.42000000000000004,"2018-06-29T11:50:59",-0.29499999999999998,{"$f":"AVERAGE(G9848:G9873)","v":-0.12692307692307692}]
[6,29,2018,11,51,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T11:51:49",-0.32500000000000001,-0.1892307692307692]
[6,29,2018,11,52,39,-0.21000000000000002,-0.21000000000000002,"2018-06-29T11:52:39",-0.22,-0.20538461538461542]
[6,29,2018,11,52,49,0.09,0.09,"2018-06-29T11:52:49",-0.155,-0.18923076923076926]
[6,29,2018,11,53,39,-0.27,-0.27,"2018-06-29T11:53:39",-0.18500000000000003,-0.22846153846153844]
[6,29,2018,11,54,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T11:54:29",-0.43500000000000005,-0.28500000000000003]
[6,29,2018,11,55,29,-0.21000000000000002,-0.21000000000000002,"2018-06-29T11:55:29",-0.39499999999999996,-0.31038461538461548]
[6,29,2018,11,56,19,-0.21000000000000002,-0.21000000000000002,"2018-06-29T11:56:19",-0.20499999999999999,-0.29653846153846158]
[6,29,2018,11,57,9,-0.09,-0.09,"2018-06-29T11:57:09",-0.16500000000000001,-0.29653846153846153]
[6,29,2018,11,57,59,-0.12,-0.12,"2018-06-29T11:57:59",-7.4999999999999997E-2,-0.26423076923076921]
[6,29,2018,11,58,49,-0.27,-0.27,"2018-06-29T11:58:49",-0.155,-0.20538461538461539]
[6,29,2018,11,59,49,0.03,0.03,"2018-06-29T11:59:49",-0.11,-0.13961538461538464]
[6,29,2018,12,0,39,0.44999999999999996,0.44999999999999996,"2018-06-29T12:00:39",0.23500000000000001,-4.7307692307692335E-2]
[6,29,2018,12,1,39,0.12,0.12,"2018-06-29T12:01:39",0.12,{"$f":"AVERAGE(G9912:G9937)","v":5.7692307692307669E-3}]
[6,29,2018,12,2,29,0.03,0.03,"2018-06-29T12:02:29",8.5000000000000006E-2,4.2692307692307682E-2]
[6,29,2018,12,3,19,-0.33,-0.33,"2018-06-29T12:03:19",-9.5000000000000015E-2,5.0769230769230754E-2]
[6,29,2018,12,3,29,-0.15000000000000002,-0.15000000000000002,"2018-06-29T12:03:29",-0.12500000000000003,5.3076923076923091E-2]
[6,29,2018,12,4,19,-0.48,-0.48,"2018-06-29T12:04:19",-0.29499999999999998,3.4160708450004819E-17]
[6,29,2018,12,5,9,-0.60000000000000009,-0.60000000000000009,"2018-06-29T12:05:09",-0.61,-0.18346153846153845]
[6,29,2018,12,6,9,-0.03,-0.03,"2018-06-29T12:06:09",-0.33,-0.28153846153846157]
[6,29,2018,12,6,59,-0.18,-0.18,"2018-06-29T12:06:59",-9.4999999999999987E-2,-0.31269230769230777]
[6,29,2018,12,7,59,0.21000000000000002,0.21000000000000002,"2018-06-29T12:07:59",2.5000000000000005E-2,-0.2630769230769231]
[6,29,2018,12,8,49,0,0,"2018-06-29T12:08:49",0.17500000000000002,-0.15807692307692306]
[6,29,2018,12,9,39,0.06,0.06,"2018-06-29T12:09:39",-6.5000000000000002E-2,-5.4230769230769221E-2]
[6,29,2018,12,10,39,-0.36,-0.36,"2018-06-29T12:10:39",-0.03,0]
[6,29,2018,12,11,19,-0.54,-0.54,"2018-06-29T12:11:19",-0.50000000000000011,-7.6153846153846169E-2]
[6,29,2018,12,12,19,-0.24,-0.24,"2018-06-29T12:12:19",-0.35000000000000003,{"$f":"AVERAGE(G9976:G10001)","v":-0.16269230769230772}]
[6,29,2018,12,13,9,0,0,"2018-06-29T12:13:09",-6.5000000000000002E-2,-0.20076923076923078]
[6,29,2018,12,13,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T12:13:59",-0.41,-0.2803846153846154]
[6,29,2018,12,14,9,-0.39,-0.39,"2018-06-29T12:14:09",-0.47500000000000003,-0.30461538461538462]
[6,29,2018,12,14,59,-0.51,-0.51,"2018-06-29T12:14:59",-0.47000000000000003,-0.38192307692307698]
[6,29,2018,12,15,49,-0.57000000000000006,-0.57000000000000006,"2018-06-29T12:15:49",-0.505,-0.36923076923076914]
[6,29,2018,12,16,49,-0.69000000000000006,-0.69000000000000006,"2018-06-29T12:16:49",-0.55000000000000004,-0.43615384615384623]
[6,29,2018,12,17,39,-0.63,-0.63,"2018-06-29T12:17:39",-0.64500000000000002,-0.53192307692307705]
[6,29,2018,12,18,39,-0.84000000000000008,-0.84000000000000008,"2018-06-29T12:18:39",-0.65,-0.57461538461538486]
[6,29,2018,12,19,29,-0.72,-0.72,"2018-06-29T12:19:29",-0.81999999999999984,-0.6346153846153848]
[6,29,2018,12,20,19,-0.48,-0.48,"2018-06-29T12:20:19",-0.59,-0.6461538461538463]
[6,29,2018,12,21,19,-0.63,-0.63,"2018-06-29T12:21:19",-0.5,-0.62884615384615394]
[6,29,2018,12,22,9,-0.33,-0.33,"2018-06-29T12:22:09",-0.46,-0.59307692307692295]
[6,29,2018,12,22,59,-0.33,-0.33,"2018-06-29T12:22:59",-0.35000000000000003,{"$f":"AVERAGE(G10040:G10065)","v":-0.53076923076923077}]
[6,29,2018,12,23,59,-0.48,-0.48,"2018-06-29T12:23:59",-0.38000000000000006,-0.43730769230769229]
[6,29,2018,12,24,49,-0.27,-0.27,"2018-06-29T12:24:49",-0.42500000000000004,-0.41307692307692301]
[6,29,2018,12,25,29,-0.27,-0.27,"2018-06-29T12:25:29",-0.30000000000000004,-0.38307692307692304]
[6,29,2018,12,25,39,-0.39,-0.39,"2018-06-29T12:25:39",-0.29000000000000004,-0.37384615384615388]
[6,29,2018,12,26,29,-0.36,-0.36,"2018-06-29T12:26:29",-0.39500000000000002,-0.36807692307692308]
[6,29,2018,12,27,29,-0.51,-0.51,"2018-06-29T12:27:29",-0.56499999999999995,-0.42000000000000004]
[6,29,2018,12,28,19,-0.24,-0.24,"2018-06-29T12:28:19",-0.38500000000000006,-0.41192307692307711]
[6,29,2018,12,29,19,-0.18,-0.18,"2018-06-29T12:29:19",-0.17500000000000002,-0.36]
[6,29,2018,12,30,9,-0.15000000000000002,-0.15000000000000002,"2018-06-29T12:30:09",-0.20499999999999999,-0.34038461538461545]
[6,29,2018,12,30,59,-0.48,-0.48,"2018-06-29T12:30:59",-0.30499999999999999,-0.32769230769230773]
[6,29,2018,12,31,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T12:31:59",-0.41999999999999993,-0.29653846153846158]
[6,29,2018,12,32,49,-0.27,-0.27,"2018-06-29T12:32:49",-0.40499999999999997,-0.31153846153846154]
[6,29,2018,12,33,39,-0.21000000000000002,-0.21000000000000002,"2018-06-29T12:33:39",-0.22499999999999998,{"$f":"AVERAGE(G10104:G10129)","v":-0.31961538461538463}]
[6,29,2018,12,34,39,-0.42000000000000004,-0.42000000000000004,"2018-06-29T12:34:39",-0.33500000000000002,-0.34846153846153832]
[6,29,2018,12,35,29,-0.39,-0.39,"2018-06-29T12:35:29",-0.37500000000000006,-0.34384615384615391]
[6,29,2018,12,35,39,-0.51,-0.51,"2018-06-29T12:35:39",-0.38999999999999996,-0.35076923076923072]
[6,29,2018,12,36,29,-0.15000000000000002,-0.15000000000000002,"2018-06-29T12:36:29",-0.33,-0.32423076923076921]
[6,29,2018,12,37,19,-0.15000000000000002,-0.15000000000000002,"2018-06-29T12:37:19",-7.5000000000000011E-2,-0.26769230769230767]
[6,29,2018,12,38,19,-0.36,-0.36,"2018-06-29T12:38:19",-0.20499999999999999,-0.25846153846153852]
[6,29,2018,12,39,9,-0.27,-0.27,"2018-06-29T12:39:09",-0.44500000000000001,-0.28153846153846157]
[6,29,2018,12,39,59,-0.21000000000000002,-0.21000000000000002,"2018-06-29T12:39:59",-0.24,-0.24923076923076926]
[6,29,2018,12,40,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T12:40:49",-0.26500000000000007,-0.2457692307692308]
[6,29,2018,12,41,39,-0.36,-0.36,"2018-06-29T12:41:39",-0.37999999999999995,-0.30576923076923079]
[6,29,2018,12,42,39,-0.63,-0.63,"2018-06-29T12:42:39",-0.34,-0.33692307692307694]
[6,29,2018,12,43,29,-0.27,-0.27,"2018-06-29T12:43:29",-0.43500000000000005,-0.32423076923076921]
[6,29,2018,12,44,19,-0.15000000000000002,-0.15000000000000002,"2018-06-29T12:44:19",-0.13499999999999998,{"$f":"AVERAGE(G10168:G10193)","v":-0.3}]
[6,29,2018,12,45,19,-0.12,-0.12,"2018-06-29T12:45:19",-0.28499999999999998,-0.29769230769230776]
[6,29,2018,12,46,9,-0.72,-0.72,"2018-06-29T12:46:09",-0.38000000000000006,-0.30923076923076925]
[6,29,2018,12,46,19,-0.78,-0.78,"2018-06-29T12:46:19",-0.49000000000000005,-0.33115384615384613]
[6,29,2018,12,47,9,-0.15000000000000002,-0.15000000000000002,"2018-06-29T12:47:09",-0.57999999999999996,-0.3576923076923077]
[6,29,2018,12,47,59,-0.54,-0.54,"2018-06-29T12:47:59",-0.34499999999999997,-0.37384615384615383]
[6,29,2018,12,48,59,-0.54,-0.54,"2018-06-29T12:48:59",-0.61499999999999999,-0.47999999999999987]
[6,29,2018,12,49,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T12:49:49",-0.42,-0.50653846153846149]
[6,29,2018,12,50,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T12:50:39",-0.37000000000000011,-0.46500000000000014]
[6,29,2018,12,51,39,-0.27,-0.27,"2018-06-29T12:51:39",{"$f":"AVERAGE(G10232:G10237)","v":-0.155},-0.39]
[6,29,2018,12,52,29,-0.39,-0.39,"2018-06-29T12:52:29",-0.33,-0.36807692307692302]
[6,29,2018,12,53,29,-0.60000000000000009,-0.60000000000000009,"2018-06-29T12:53:29",-0.45500000000000002,-0.33576923076923076]
[6,29,2018,12,54,9,-0.15000000000000002,-0.15000000000000002,"2018-06-29T12:54:09",-0.50000000000000011,-0.34615384615384615]
[6,29,2018,12,54,59,-0.27,-0.27,"2018-06-29T12:54:59",-0.215,{"$f":"AVERAGE(G10232:G10257)","v":-0.32076923076923081}]
[6,29,2018,12,55,59,-0.06,-0.06,"2018-06-29T12:55:59",-9.5000000000000015E-2,-0.30692307692307691]
[6,29,2018,12,56,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T12:56:49",-0.16500000000000001,-0.27692307692307688]
[6,29,2018,12,56,59,-0.24,-0.24,"2018-06-29T12:56:59",-0.19499999999999998,-0.26999999999999996]
[6,29,2018,12,57,49,0.03,0.03,"2018-06-29T12:57:49",-9.4999999999999987E-2,-0.19384615384615389]
[6,29,2018,12,58,39,-0.21000000000000002,-0.21000000000000002,"2018-06-29T12:58:39",-6.0000000000000005E-2,-0.12807692307692309]
[6,29,2018,12,59,39,-0.03,-0.03,"2018-06-29T12:59:39",-5.000000000000001E-2,-0.09]
[6,29,2018,13,0,29,-0.21000000000000002,-0.21000000000000002,"2018-06-29T13:00:29",-0.12,-0.1073076923076923]
[6,29,2018,13,1,19,-0.24,-0.24,"2018-06-29T13:01:19",-0.17,-9.6923076923076945E-2]
[6,29,2018,13,2,19,-0.39,-0.39,"2018-06-29T13:02:19",{"$f":"AVERAGE(G10296:G10301)","v":-0.24},-0.14423076923076927]
[6,29,2018,13,3,9,-0.51,-0.51,"2018-06-29T13:03:09",-0.38999999999999996,-0.18807692307692303]
[6,29,2018,13,4,9,-0.48,-0.48,"2018-06-29T13:04:09",-0.3,-0.25730769230769229]
[6,29,2018,13,4,59,0.66,0.66,"2018-06-29T13:04:59",-0.11,-0.23423076923076921]
[6,29,2018,13,5,49,-0.69000000000000006,-0.69000000000000006,"2018-06-29T13:05:49",-0.25,-0.28500000000000003]
[6,29,2018,13,6,49,-0.36,-0.36,"2018-06-29T13:06:49",-0.7599999999999999,-0.39230769230769236]
[6,29,2018,13,7,39,-0.57000000000000006,-0.57000000000000006,"2018-06-29T13:07:39",-0.53500000000000003,-0.42]
[6,29,2018,13,8,19,-0.33,-0.33,"2018-06-29T13:08:19",-0.45500000000000007,-0.45692307692307693]
[6,29,2018,13,8,29,-0.12,-0.12,"2018-06-29T13:08:29",-0.39000000000000007,-0.44307692307692315]
[6,29,2018,13,9,19,-0.48,-0.48,"2018-06-29T13:09:19",-0.22500000000000001,-0.4834615384615385]
[6,29,2018,13,10,19,-0.42000000000000004,-0.42000000000000004,"2018-06-29T13:10:19",-0.40499999999999997,-0.46499999999999997]
[6,29,2018,13,11,9,-0.75,-0.75,"2018-06-29T13:11:09",-0.45500000000000002,-0.40730769230769232]
[6,29,2018,13,11,59,-0.84000000000000008,-0.84000000000000008,"2018-06-29T13:11:59",-0.72000000000000008,-0.435]
[6,29,2018,13,12,59,-0.72,-0.72,"2018-06-29T13:12:59",{"$f":"AVERAGE(G10360:G10365)","v":-0.77499999999999991},-0.53884615384615386]
[6,29,2018,13,13,49,-0.66,-0.66,"2018-06-29T13:13:49",-0.67,-0.60692307692307701]
[6,29,2018,13,14,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T13:14:49",-0.62499999999999989,-0.66346153846153844]
[6,29,2018,13,15,39,-0.39,-0.39,"2018-06-29T13:15:39",-0.62,-0.69346153846153846]
[6,29,2018,13,16,29,-0.18,-0.18,"2018-06-29T13:16:29",-0.38500000000000001,-0.62307692307692308]
[6,29,2018,13,17,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T13:17:29",-0.53500000000000003,-0.57115384615384612]
[6,29,2018,13,18,19,-0.24,-0.24,"2018-06-29T13:18:19",-0.31,-0.50538461538461532]
[6,29,2018,13,19,9,0.03,0.03,"2018-06-29T13:19:09",-0.19000000000000003,-0.41423076923076935]
[6,29,2018,13,19,19,0.06,0.06,"2018-06-29T13:19:19",-0.14000000000000001,-0.37961538461538463]
[6,29,2018,13,20,9,-0.18,-0.18,"2018-06-29T13:20:09",-8.5000000000000006E-2,-0.28846153846153844]
[6,29,2018,13,21,9,-0.72,-0.72,"2018-06-29T13:21:09",-0.58499999999999996,-0.33230769230769225]
[6,29,2018,13,21,59,-0.42000000000000004,-0.42000000000000004,"2018-06-29T13:21:59",-0.59500000000000008,-0.33692307692307699]
[6,29,2018,13,22,49,-0.33,-0.33,"2018-06-29T13:22:49",-0.45999999999999996,-0.37615384615384612]
[6,29,2018,13,23,39,-0.51,-0.51,"2018-06-29T13:23:39",{"$f":"AVERAGE(G10424:G10429)","v":-0.42499999999999999},-0.44192307692307692]
[6,29,2018,13,24,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T13:24:29",-0.62000000000000011,-0.54346153846153844]
[6,29,2018,13,25,29,-0.69000000000000006,-0.69000000000000006,"2018-06-29T13:25:29",-0.69500000000000017,-0.56884615384615378]
[6,29,2018,13,26,19,-0.75,-0.75,"2018-06-29T13:26:19",-0.77999999999999992,-0.61269230769230765]
[6,29,2018,13,27,9,-0.06,-0.06,"2018-06-29T13:27:09",-0.36500000000000005,-0.57807692307692315]
[6,29,2018,13,28,9,-0.51,-0.51,"2018-06-29T13:28:09",-0.31500000000000006,-0.54692307692307707]
[6,29,2018,13,28,59,-0.30000000000000004,-0.30000000000000004,"2018-06-29T13:28:59",-0.56999999999999995,-0.52500000000000024]
[6,29,2018,13,29,49,-0.69000000000000006,-0.69000000000000006,"2018-06-29T13:29:49",-0.54500000000000004,-0.50769230769230766]
[6,29,2018,13,29,59,-0.63,-0.63,"2018-06-29T13:29:59",-0.6,-0.49961538461538463]
[6,29,2018,13,30,49,-0.51,-0.51,"2018-06-29T13:30:49",-0.5,-0.44653846153846161]
[6,29,2018,13,31,49,-0.48,-0.48,"2018-06-29T13:31:49",-0.31,-0.47307692307692306]
[6,29,2018,13,32,39,-0.60000000000000009,-0.60000000000000009,"2018-06-29T13:32:39",-0.43500000000000005,-0.46846153846153843]
[6,29,2018,13,33,29,-0.48,-0.48,"2018-06-29T13:33:29",-0.41,-0.43384615384615388]
[6,29,2018,13,34,29,-0.44999999999999996,-0.44999999999999996,"2018-06-29T13:34:29",-0.34,-0.37615384615384617]
[6,29,2018,13,35,19,-0.78,-0.78,"2018-06-29T13:35:19",-0.45999999999999996,-0.37500000000000006]
[6,29,2018,13,36,9,-0.54,-0.54,"2018-06-29T13:36:09",-0.7400000000000001,-0.46153846153846156]
[6,29,2018,13,36,59,-0.48,-0.48,"2018-06-29T13:36:59",-0.38000000000000006,-0.44653846153846166]
[6,29,2018,13,37,49,-0.21000000000000002,-0.21000000000000002,"2018-06-29T13:37:49",-0.46,-0.46269230769230785]
[6,29,2018,13,38,49,-0.15000000000000002,-0.15000000000000002,"2018-06-29T13:38:49",-0.25500000000000006,-0.44307692307692315]
[6,29,2018,13,39,39,-0.48,-0.48,"2018-06-29T13:39:39",-0.435,-0.44884615384615389]
[6,29,2018,13,40,29,-0.66,-0.66,"2018-06-29T13:40:29",-0.62500000000000011,-0.43384615384615388]
[6,29,2018,13,40,39,-0.75,-0.75,"2018-06-29T13:40:39",-0.67,-0.45000000000000007]
[6,29,2018,13,41,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T13:41:29",-0.59000000000000008,-0.47769230769230769]
[6,29,2018,13,42,29,-0.27,-0.27,"2018-06-29T13:42:29",-0.36499999999999999,-0.47076923076923083]
[6,29,2018,13,43,19,-0.42000000000000004,-0.42000000000000004,"2018-06-29T13:43:19",-0.56999999999999995,-0.55730769230769239]
[6,29,2018,13,44,9,-0.42000000000000004,-0.42000000000000004,"2018-06-29T13:44:09",-0.37000000000000005,-0.5065384615384616]
[6,29,2018,13,45,9,-0.89999999999999991,-0.89999999999999991,"2018-06-29T13:45:09",-0.68,-0.51692307692307704]
[6,29,2018,13,45,59,-0.63,-0.63,"2018-06-29T13:45:59",-0.74500000000000011,-0.55269230769230782]
[6,29,2018,13,46,49,-1.0499999999999998,-1.0499999999999998,"2018-06-29T13:46:49",-0.73,-0.62884615384615394]
[6,29,2018,13,47,49,-0.54,-0.54,"2018-06-29T13:47:49",-0.55500000000000005,-0.63115384615384607]
[6,29,2018,13,48,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T13:48:39",-0.38499999999999995,-0.61615384615384605]
[6,29,2018,13,49,39,0.06,0.06,"2018-06-29T13:49:39",-8.5000000000000006E-2,-0.46499999999999997]
[6,29,2018,13,50,29,-0.15000000000000002,-0.15000000000000002,"2018-06-29T13:50:29",-9.9999999999999992E-2,-0.36692307692307696]
[6,29,2018,13,51,19,-0.60000000000000009,-0.60000000000000009,"2018-06-29T13:51:19",-0.13500000000000004,-0.23653846153846156]
[6,29,2018,13,51,29,-0.78,-0.78,"2018-06-29T13:51:29",-0.24000000000000002,-0.24692307692307697]
[6,29,2018,13,52,9,-0.78,-0.78,"2018-06-29T13:52:09",-0.82500000000000007,-0.30576923076923085]
[6,29,2018,13,53,9,-0.44999999999999996,-0.44999999999999996,"2018-06-29T13:53:09",-0.54,-0.35076923076923072]
[6,29,2018,13,53,59,-0.81,-0.81,"2018-06-29T13:53:59",-0.53999999999999992,-0.45000000000000007]
[6,29,2018,13,54,49,-0.99,-0.99,"2018-06-29T13:54:49",-0.87000000000000011,-0.59423076923076923]
[6,29,2018,13,55,49,-0.48,-0.48,"2018-06-29T13:55:49",-0.77999999999999992,-0.71884615384615391]
[6,29,2018,13,56,39,-0.36,-0.36,"2018-06-29T13:56:39",-0.44500000000000001,-0.63923076923076916]
[6,29,2018,13,57,29,-0.39,-0.39,"2018-06-29T13:57:29",-0.55000000000000004,-0.65423076923076928]
[6,29,2018,13,58,29,-0.39,-0.39,"2018-06-29T13:58:29",-0.26500000000000007,-0.57461538461538453]
[6,29,2018,13,59,19,-0.27,-0.27,"2018-06-29T13:59:19",-0.41000000000000009,-0.4834615384615385]
[6,29,2018,14,0,19,-0.51,-0.51,"2018-06-29T14:00:19",-0.26,-0.38653846153846144]
[6,29,2018,14,1,9,-0.44999999999999996,-0.44999999999999996,"2018-06-29T14:01:09",-0.40000000000000008,-0.36346153846153845]
[6,29,2018,14,1,59,-0.81,-0.81,"2018-06-29T14:01:59",-0.77,-0.42692307692307696]
[6,29,2018,14,2,9,-0.89999999999999991,-0.89999999999999991,"2018-06-29T14:02:09",-0.84500000000000008,-0.45230769230769241]
[6,29,2018,14,2,59,-0.54,-0.54,"2018-06-29T14:02:59",-0.69499999999999995,-0.51]
[6,29,2018,14,3,49,-0.51,-0.51,"2018-06-29T14:03:49",-0.6,-0.5607692307692308]
[6,29,2018,14,4,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T14:04:49",-0.48,-0.60115384615384615]
[6,29,2018,14,5,39,-0.36,-0.36,{"$f":"DATE(C10681,A10681,B10681)+TIME(D10681,E10681,F10681)","v":"2018-06-29T14:05:39"},-0.38999999999999996,-0.60115384615384626]
[6,29,2018,14,6,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T14:06:29",-0.45500000000000007,-0.52384615384615385]
[6,29,2018,14,7,19,-0.44999999999999996,-0.44999999999999996,"2018-06-29T14:07:19",-0.56500000000000006,-0.5065384615384616]
[6,29,2018,14,8,9,-0.78,-0.78,"2018-06-29T14:08:09",-0.56499999999999995,-0.50192307692307692]
[6,29,2018,14,9,9,-0.66,-0.66,"2018-06-29T14:09:09",-0.72499999999999998,-0.55846153846153834]
[6,29,2018,14,9,59,-0.75,-0.75,"2018-06-29T14:09:59",-0.77500000000000002,-0.63346153846153841]
[6,29,2018,14,10,59,-0.89999999999999991,-0.89999999999999991,"2018-06-29T14:10:59",-0.86999999999999977,-0.7188461538461538]
[6,29,2018,14,11,49,-0.63,-0.63,"2018-06-29T14:11:49",-0.81999999999999984,-0.76961538461538459]
[6,29,2018,14,12,39,-0.18,-0.18,"2018-06-29T14:12:39",-0.505,-0.73499999999999988]
[6,29,2018,14,12,49,-0.18,-0.18,"2018-06-29T14:12:49",-0.43,-0.70846153846153836]
[6,29,2018,14,13,39,-0.27,-0.27,"2018-06-29T14:13:39",-0.24000000000000002,-0.63000000000000012]
[6,29,2018,14,14,29,-0.33,-0.33,"2018-06-29T14:14:29",-0.33500000000000002,-0.53653846153846163]
[6,29,2018,14,15,29,-0.60000000000000009,-0.60000000000000009,"2018-06-29T14:15:29",-0.32,-0.40615384615384598]
[6,29,2018,14,16,19,-0.24,-0.24,{"$f":"DATE(C10745,A10745,B10745)+TIME(D10745,E10745,F10745)","v":"2018-06-29T14:16:19"},-0.67,-0.40153846153846157]
[6,29,2018,14,17,19,-0.51,-0.51,"2018-06-29T14:17:19",-0.47499999999999992,-0.42230769230769233]
[6,29,2018,14,18,9,-0.44999999999999996,-0.44999999999999996,"2018-06-29T14:18:09",-0.43500000000000005,-0.45230769230769224]
[6,29,2018,14,18,59,-0.54,-0.54,"2018-06-29T14:18:59",-0.52,-0.48807692307692296]
[6,29,2018,14,19,49,-0.96,-0.96,"2018-06-29T14:19:49",-0.64,-0.55153846153846153]
[6,29,2018,14,20,39,-0.75,-0.75,"2018-06-29T14:20:39",-0.83499999999999996,-0.57576923076923081]
[6,29,2018,14,21,29,-0.51,-0.51,"2018-06-29T14:21:29",-0.73999999999999988,-0.62769230769230788]
[6,29,2018,14,22,29,-0.48,-0.48,"2018-06-29T14:22:29",-0.38000000000000006,-0.61499999999999999]
[6,29,2018,14,23,19,-0.54,-0.54,"2018-06-29T14:23:19",-0.46,-0.60000000000000009]
[6,29,2018,14,23,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T14:23:29",-0.45,-0.59538461538461551]
[6,29,2018,14,24,19,-0.09,-0.09,"2018-06-29T14:24:19",-0.34,-0.52038461538461545]
[6,29,2018,14,25,9,-0.54,-0.54,"2018-06-29T14:25:09",-0.31,-0.43730769230769223]
[6,29,2018,14,26,9,-0.44999999999999996,-0.44999999999999996,"2018-06-29T14:26:09",-0.58499999999999996,-0.42461538461538456]
[6,29,2018,14,26,59,-0.75,-0.75,{"$f":"DATE(C10809,A10809,B10809)+TIME(D10809,E10809,F10809)","v":"2018-06-29T14:26:59"},-0.54999999999999993,-0.46269230769230768]
[6,29,2018,14,27,59,-0.51,-0.51,"2018-06-29T14:27:59",-0.66499999999999992,-0.51230769230769235]
[6,29,2018,14,28,49,-0.51,-0.51,"2018-06-29T14:28:49",-0.65499999999999992,-0.59076923076923071]
[6,29,2018,14,29,39,-0.69000000000000006,-0.69000000000000006,"2018-06-29T14:29:39",-0.56500000000000006,-0.61961538461538457]
[6,29,2018,14,30,39,-0.69000000000000006,-0.69000000000000006,"2018-06-29T14:30:39",-0.71499999999999997,-0.653076923076923]
[6,29,2018,14,31,29,-0.78,-0.78,"2018-06-29T14:31:29",-0.77999999999999992,-0.68076923076923079]
[6,29,2018,14,32,19,-0.72,-0.72,"2018-06-29T14:32:19",-0.82,-0.72]
[6,29,2018,14,33,19,-0.69000000000000006,-0.69000000000000006,"2018-06-29T14:33:19",-0.76500000000000012,-0.74538461538461531]
[6,29,2018,14,34,9,-0.18,-0.18,"2018-06-29T14:34:09",-0.49500000000000005,-0.7153846153846154]
[6,29,2018,14,34,19,-0.12,-0.12,"2018-06-29T14:34:19",-0.40000000000000008,-0.69230769230769229]
[6,29,2018,14,34,59,-0.36,-0.36,"2018-06-29T14:34:59",-0.315,-0.64269230769230767]
[6,29,2018,14,35,49,-0.54,-0.54,"2018-06-29T14:35:49",-0.32,-0.54923076923076919]
[6,29,2018,14,36,49,0,0,"2018-06-29T14:36:49",5.5E-2,-0.34846153846153849]
[6,29,2018,14,37,39,-1.2000000000000002,-1.2000000000000002,{"$f":"DATE(C10873,A10873,B10873)+TIME(D10873,E10873,F10873)","v":"2018-06-29T14:37:39"},-0.73,-0.36923076923076914]
[6,29,2018,14,38,39,-1.0499999999999998,-1.0499999999999998,"2018-06-29T14:38:39",-0.96,-0.49846153846153851]
[6,29,2018,14,39,29,-1.17,-1.17,"2018-06-29T14:39:29",-1.1100000000000001,-0.6449999999999998]
[6,29,2018,14,40,19,-1.26,-1.26,"2018-06-29T14:40:19",-1.0549999999999999,-0.78923076923076918]
[6,29,2018,14,41,19,-0.78,-0.78,"2018-06-29T14:41:19",-0.82,-0.9853846153846153]
[6,29,2018,14,42,9,-0.66,-0.66,"2018-06-29T14:42:09",-0.71,-0.91961538461538461]
[6,29,2018,14,42,59,-0.27,-0.27,"2018-06-29T14:42:59",-0.53999999999999992,-0.83653846153846168]
[6,29,2018,14,43,59,-0.12,-0.12,"2018-06-29T14:43:59",-0.12000000000000001,-0.60461538461538455]
[6,29,2018,14,44,49,-0.81,-0.81,"2018-06-29T14:44:49",-0.26,-0.47423076923076923]
[6,29,2018,14,44,59,-0.92999999999999994,-0.92999999999999994,"2018-06-29T14:44:59",-0.39500000000000002,-0.48461538461538461]
[6,29,2018,14,45,49,-0.75,-0.75,"2018-06-29T14:45:49",-0.66499999999999992,-0.4407692307692308]
[6,29,2018,14,46,39,-0.27,-0.27,"2018-06-29T14:46:39",-0.36500000000000005,-0.36115384615384616]
[6,29,2018,14,47,39,-0.06,-0.06,"2018-06-29T14:47:39",-0.25500000000000006,-0.33807692307692311]
[6,29,2018,14,48,29,-0.12,-0.12,"2018-06-29T14:48:29",-9.4999999999999987E-2,-0.33461538461538454]
[6,29,2018,14,49,9,0.06,0.06,"2018-06-29T14:49:09",-0.04,-0.28269230769230769]
[6,29,2018,14,50,9,-0.48,-0.48,"2018-06-29T14:50:09",-0.32,-0.20307692307692313]
[6,29,2018,14,50,59,-0.33,-0.33,"2018-06-29T14:50:59",-0.44500000000000001,-0.23192307692307693]
[6,29,2018,14,51,59,-0.60000000000000009,-0.60000000000000009,"2018-06-29T14:51:59",-0.43,-0.27230769230769231]
[6,29,2018,14,52,49,-0.66,-0.66,"2018-06-29T14:52:49",-0.58500000000000008,-0.36461538461538462]
[6,29,2018,14,53,39,-0.60000000000000009,-0.60000000000000009,"2018-06-29T14:53:39",-0.6100000000000001,-0.48230769230769227]
[6,29,2018,14,54,39,-0.48,-0.48,"2018-06-29T14:54:39",-0.56000000000000005,-0.52153846153846162]
[6,29,2018,14,55,29,-0.36,-0.36,"2018-06-29T14:55:29",-0.41,-0.51692307692307715]
[6,29,2018,14,55,39,-0.42000000000000004,-0.42000000000000004,"2018-06-29T14:55:39",-0.39999999999999997,-0.51692307692307704]
[6,29,2018,14,56,29,-0.60000000000000009,-0.60000000000000009,"2018-06-29T14:56:29",-0.51500000000000001,-0.52961538461538482]
[6,29,2018,14,57,19,-0.60000000000000009,-0.60000000000000009,"2018-06-29T14:57:19",-0.55500000000000005,-0.52153846153846173]
[6,29,2018,14,58,19,-0.60000000000000009,-0.60000000000000009,"2018-06-29T14:58:19",-0.55500000000000005,-0.50769230769230755]
[6,29,2018,14,59,9,-0.75,-0.75,"2018-06-29T14:59:09",-0.62,-0.53192307692307694]
[6,29,2018,14,59,59,-0.36,-0.36,"2018-06-29T14:59:59",-0.53500000000000003,-0.55038461538461536]
[6,29,2018,15,0,59,-0.42000000000000004,-0.42000000000000004,"2018-06-29T15:00:59",-0.38000000000000006,-0.51115384615384618]
[6,29,2018,15,1,49,-0.99,-0.99,"2018-06-29T15:01:49",-0.56999999999999995,-0.52038461538461545]
[6,29,2018,15,2,49,-0.89999999999999991,-0.89999999999999991,"2018-06-29T15:02:49",-0.71,-0.55730769230769239]
[6,29,2018,15,3,39,-0.78,-0.78,"2018-06-29T15:03:39",-0.85499999999999998,-0.58846153846153837]
[6,29,2018,15,4,19,-0.12,-0.12,"2018-06-29T15:04:19",-0.51500000000000012,-0.58615384615384614]
[6,29,2018,15,5,19,-0.89999999999999991,-0.89999999999999991,"2018-06-29T15:05:19",-0.29499999999999998,-0.56653846153846166]
[6,29,2018,15,6,9,-0.57000000000000006,-0.57000000000000006,"2018-06-29T15:06:09",-0.68,-0.57346153846153858]
[6,29,2018,15,6,59,-0.60000000000000009,-0.60000000000000009,"2018-06-29T15:06:59",-0.69999999999999984,-0.5838461538461539]
[6,29,2018,15,7,9,-1.17,-1.17,"2018-06-29T15:07:09",-0.80000000000000016,-0.59423076923076923]
[6,29,2018,15,7,59,-0.92999999999999994,-0.92999999999999994,"2018-06-29T15:07:59",-0.79499999999999993,-0.56999999999999995]
[6,29,2018,15,8,59,-0.69000000000000006,-0.69000000000000006,"2018-06-29T15:08:59",-0.77,-0.68307692307692314]
[6,29,2018,15,9,49,-0.44999999999999996,-0.44999999999999996,"2018-06-29T15:09:49",-0.59500000000000008,-0.70153846153846167]
[6,29,2018,15,10,39,-0.42000000000000004,-0.42000000000000004,"2018-06-29T15:10:39",-0.40000000000000008,-0.63230769230769235]
[6,29,2018,15,11,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T15:11:39",-0.6,-0.62076923076923074]
[6,29,2018,15,12,29,-0.63,-0.63,"2018-06-29T15:12:29",-0.49499999999999994,-0.55961538461538463]
[6,29,2018,15,13,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T15:13:29",-0.66,-0.5526923076923077]
[6,29,2018,15,14,19,-0.69000000000000006,-0.69000000000000006,"2018-06-29T15:14:19",-0.69000000000000006,-0.5873076923076922]
[6,29,2018,15,15,9,-0.63,-0.63,"2018-06-29T15:15:09",-0.64999999999999991,-0.63115384615384607]
[6,29,2018,15,16,9,-0.18,-0.18,"2018-06-29T15:16:09",-0.435,-0.59653846153846146]
[6,29,2018,15,16,59,-0.12,-0.12,"2018-06-29T15:16:59",-0.22999999999999998,-0.52846153846153843]
[6,29,2018,15,17,9,-0.24,-0.24,"2018-06-29T15:17:09",-0.24000000000000002,-0.51115384615384607]
[6,29,2018,15,17,49,-0.33,-0.33,"2018-06-29T15:17:49",-0.22500000000000001,-0.45461538461538464]
[6,29,2018,15,18,39,-0.66,-0.66,"2018-06-29T15:18:39",-0.51500000000000001,-0.4234615384615385]
[6,29,2018,15,19,39,-0.89999999999999991,-0.89999999999999991,"2018-06-29T15:19:39",-0.81500000000000006,-0.46269230769230774]
[6,29,2018,15,20,29,-0.69000000000000006,-0.69000000000000006,"2018-06-29T15:20:29",-0.75499999999999989,-0.52730769230769237]
[6,29,2018,15,21,19,-0.89999999999999991,-0.89999999999999991,"2018-06-29T15:21:19",-0.76500000000000001,-0.63115384615384618]
[6,29,2018,15,22,19,-0.48,-0.48,"2018-06-29T15:22:19",-0.83499999999999996,-0.7580769230769232]
[6,29,2018,15,23,9,-0.69000000000000006,-0.69000000000000006,"2018-06-29T15:23:09",-0.51999999999999991,-0.74192307692307691]
[6,29,2018,15,24,9,-0.81,-0.81,"2018-06-29T15:24:09",-0.77999999999999992,-0.73269230769230775]
[6,29,2018,15,24,59,-0.84000000000000008,-0.84000000000000008,"2018-06-29T15:24:59",-0.90999999999999981,-0.77769230769230768]
[6,29,2018,15,25,49,-0.99,-0.99,"2018-06-29T15:25:49",-0.8849999999999999,-0.78576923076923066]
[6,29,2018,15,26,49,-1.02,-1.02,"2018-06-29T15:26:49",-0.91500000000000004,-0.82615384615384591]
[6,29,2018,15,27,39,-0.89999999999999991,-0.89999999999999991,"2018-06-29T15:27:39",-0.85500000000000009,-0.87230769230769212]
[6,29,2018,15,28,29,-0.51,-0.51,"2018-06-29T15:28:29",-0.69499999999999995,-0.84576923076923083]
[6,29,2018,15,28,39,-0.57000000000000006,-0.57000000000000006,"2018-06-29T15:28:39",-0.64,-0.8353846153846155]
[6,29,2018,15,29,29,-0.60000000000000009,-0.60000000000000009,"2018-06-29T15:29:29",-0.70000000000000007,-0.79846153846153867]
[6,29,2018,15,30,29,-0.84000000000000008,-0.84000000000000008,"2018-06-29T15:30:29",-0.73000000000000009,-0.7580769230769232]
[6,29,2018,15,31,19,-0.66,-0.66,"2018-06-29T15:31:19",-0.78500000000000014,-0.72115384615384603]
[6,29,2018,15,31,59,-0.42000000000000004,-0.42000000000000004,"2018-06-29T15:31:59",-0.64500000000000002,-0.69692307692307698]
[6,29,2018,15,32,59,-0.63,-0.63,"2018-06-29T15:32:59",-0.5099999999999999,-0.66692307692307706]
[6,29,2018,15,33,49,-0.63,-0.63,"2018-06-29T15:33:49",-0.77999999999999992,-0.68307692307692314]
[6,29,2018,15,34,39,-0.44999999999999996,-0.44999999999999996,"2018-06-29T15:34:39",-0.56000000000000005,-0.65192307692307705]
[6,29,2018,15,35,39,-0.54,-0.54,"2018-06-29T15:35:39",-0.42499999999999999,-0.56884615384615367]
[6,29,2018,15,36,29,-0.54,-0.54,"2018-06-29T15:36:29",-0.56000000000000005,-0.56653846153846144]
[6,29,2018,15,37,29,-0.72,-0.72,"2018-06-29T15:37:29",-0.58499999999999996,-0.57692307692307709]
[6,29,2018,15,38,19,-0.12,-0.12,"2018-06-29T15:38:19",-0.47500000000000003,-0.50192307692307703]
[6,29,2018,15,39,9,-0.48,-0.48,"2018-06-29T15:39:09",-0.34500000000000003,-0.48115384615384638]
[6,29,2018,15,39,19,-0.44999999999999996,-0.44999999999999996,"2018-06-29T15:39:19",-0.40000000000000008,-0.49384615384615399]
[6,29,2018,15,40,9,-0.24,-0.24,"2018-06-29T15:40:09",-0.40000000000000008,-0.47307692307692312]
[6,29,2018,15,41,9,-0.24,-0.24,"2018-06-29T15:41:09",-0.18000000000000002,-0.38423076923076926]
[6,29,2018,15,41,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T15:41:59",-0.34500000000000003,-0.33692307692307694]
[6,29,2018,15,42,49,-0.81,-0.81,"2018-06-29T15:42:49",-0.64,-0.40384615384615391]
[6,29,2018,15,43,49,-0.51,-0.51,"2018-06-29T15:43:49",-0.6349999999999999,-0.45115384615384618]
[6,29,2018,15,44,39,-0.42000000000000004,-0.42000000000000004,"2018-06-29T15:44:39",-0.51500000000000001,-0.48115384615384615]
[6,29,2018,15,45,29,-0.36,-0.36,"2018-06-29T15:45:29",-0.375,-0.51692307692307693]
[6,29,2018,15,46,29,-0.24,-0.24,"2018-06-29T15:46:29",-0.36000000000000004,-0.5030769230769232]
[6,29,2018,15,47,9,-0.51,-0.51,"2018-06-29T15:47:09",-0.30499999999999999,-0.44884615384615389]
[6,29,2018,15,48,9,-0.60000000000000009,-0.60000000000000009,"2018-06-29T15:48:09",-0.61,-0.44307692307692303]
[6,29,2018,15,48,59,-0.78,-0.78,"2018-06-29T15:48:59",-0.72500000000000009,-0.48807692307692307]
[6,29,2018,15,49,49,-0.44999999999999996,-0.44999999999999996,"2018-06-29T15:49:49",-0.745,-0.55961538461538463]
[6,29,2018,15,49,59,-0.36,-0.36,"2018-06-29T15:49:59",-0.67499999999999993,-0.56192307692307686]
[6,29,2018,15,50,49,-0.54,-0.54,"2018-06-29T15:50:49",-0.40000000000000008,-0.568846153846154]
[6,29,2018,15,51,49,-0.54,-0.54,"2018-06-29T15:51:49",-0.61499999999999999,-0.61384615384615415]
[6,29,2018,15,52,39,-0.69000000000000006,-0.69000000000000006,"2018-06-29T15:52:39",-0.54500000000000004,-0.59653846153846168]
[6,29,2018,15,53,29,-0.44999999999999996,-0.44999999999999996,"2018-06-29T15:53:29",-0.54500000000000004,-0.54692307692307685]
[6,29,2018,15,54,29,-0.60000000000000009,-0.60000000000000009,"2018-06-29T15:54:29",-0.52,-0.52846153846153832]
[6,29,2018,15,55,19,-0.57000000000000006,-0.57000000000000006,"2018-06-29T15:55:19",-0.6150000000000001,-0.5607692307692308]
[6,29,2018,15,56,9,-0.54,-0.54,"2018-06-29T15:56:09",-0.59500000000000008,-0.55846153846153845]
[6,29,2018,15,57,9,-0.39,-0.39,"2018-06-29T15:57:09",-0.45500000000000002,-0.53538461538461535]
[6,29,2018,15,57,59,-0.30000000000000004,-0.30000000000000004,"2018-06-29T15:57:59",-0.24000000000000002,-0.48115384615384615]
[6,29,2018,15,58,59,-0.60000000000000009,-0.60000000000000009,"2018-06-29T15:58:59",-0.41,-0.44884615384615378]
[6,29,2018,15,59,49,-0.51,-0.51,"2018-06-29T15:59:49",-0.66,-0.45923076923076928]
[6,29,2018,15,59,59,-0.54,-0.54,"2018-06-29T15:59:59",-0.64999999999999991,-0.45692307692307704]
[6,29,2018,16,0,39,-0.51,-0.51,"2018-06-29T16:00:39",-0.51500000000000001,-0.44769230769230767]
[6,29,2018,16,1,29,-0.48,-0.48,"2018-06-29T16:01:29",-0.45,-0.44769230769230778]
[6,29,2018,16,2,19,-0.39,-0.39,"2018-06-29T16:02:19",-0.44500000000000001,-0.49153846153846159]
[6,29,2018,16,3,19,-0.18,-0.18,"2018-06-29T16:03:19",-0.28499999999999998,-0.46269230769230774]
[6,29,2018,16,4,9,-0.18,-0.18,"2018-06-29T16:04:09",-0.245,-0.38307692307692304]
[6,29,2018,16,5,9,-0.66,-0.66,"2018-06-29T16:05:09",-0.48,-0.37615384615384612]
[6,29,2018,16,5,59,-0.27,-0.27,"2018-06-29T16:05:59",-0.59000000000000008,-0.40269230769230774]
[6,29,2018,16,6,49,-0.36,-0.36,"2018-06-29T16:06:49",-0.25,-0.3692307692307692]
[6,29,2018,16,7,49,-0.99,-0.99,"2018-06-29T16:07:49",-0.71,-0.47423076923076929]
[6,29,2018,16,8,39,-1.1099999999999999,-1.1099999999999999,"2018-06-29T16:08:39",-1.1349999999999998,-0.64961538461538459]
[6,29,2018,16,9,39,-0.72,-0.72,"2018-06-29T16:09:39",-0.73499999999999988,-0.68423076923076909]
[6,29,2018,16,10,29,-0.63,-0.63,"2018-06-29T16:10:29",-0.64500000000000002,-0.71192307692307688]
[6,29,2018,16,11,19,-0.57000000000000006,-0.57000000000000006,"2018-06-29T16:11:19",-0.67,-0.7926923076923077]
[6,29,2018,16,11,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T16:11:29",-0.66,-0.79384615384615387]
[6,29,2018,16,12,19,-0.66,-0.66,"2018-06-29T16:12:19",-0.61,-0.74769230769230788]
[6,29,2018,16,13,9,-0.60000000000000009,-0.60000000000000009,"2018-06-29T16:13:09",-0.63,-0.65192307692307705]
[6,29,2018,16,14,9,-0.63,-0.63,"2018-06-29T16:14:09",-0.69500000000000017,-0.64730769230769236]
[6,29,2018,16,15,9,-0.60000000000000009,-0.60000000000000009,"2018-06-29T16:15:09",-0.67500000000000016,-0.65423076923076928]
[6,29,2018,16,15,49,-0.44999999999999996,-0.44999999999999996,"2018-06-29T16:15:49",-0.57500000000000007,-0.63692307692307704]
[6,29,2018,16,16,39,-0.44999999999999996,-0.44999999999999996,"2018-06-29T16:16:39",-0.45999999999999996,-0.60692307692307679]
[6,29,2018,16,17,29,-0.51,-0.51,"2018-06-29T16:17:29",-0.5,-0.58499999999999996]
[6,29,2018,16,18,29,-0.51,-0.51,"2018-06-29T16:18:29",-0.5,-0.53999999999999992]
[6,29,2018,16,19,19,-0.39,-0.39,"2018-06-29T16:19:19",-0.40500000000000003,-0.48115384615384615]
[6,29,2018,16,20,9,-0.54,-0.54,"2018-06-29T16:20:09",-0.43500000000000005,-0.46153846153846156]
[6,29,2018,16,21,9,-0.69000000000000006,-0.69000000000000006,"2018-06-29T16:21:09",-0.6150000000000001,-0.49615384615384606]
[6,29,2018,16,21,59,-0.69000000000000006,-0.69000000000000006,"2018-06-29T16:21:59",-0.73499999999999999,-0.54230769230769227]
[6,29,2018,16,22,9,-0.72,-0.72,"2018-06-29T16:22:09",-0.7400000000000001,-0.55038461538461536]
[6,29,2018,16,22,59,-0.66,-0.66,"2018-06-29T16:22:59",-0.72000000000000008,-0.59076923076923082]
[6,29,2018,16,23,49,-0.69000000000000006,-0.69000000000000006,"2018-06-29T16:23:49",-0.72500000000000009,-0.66346153846153855]
[6,29,2018,16,24,49,-0.72,-0.72,"2018-06-29T16:24:49",-0.69499999999999995,-0.70846153846153836]
[6,29,2018,16,25,39,-0.51,-0.51,"2018-06-29T16:25:39",-0.58499999999999996,-0.69000000000000006]
[6,29,2018,16,26,39,-0.60000000000000009,-0.60000000000000009,"2018-06-29T16:26:39",-0.58500000000000008,-0.65423076923076928]
[6,29,2018,16,27,29,-0.39,-0.39,"2018-06-29T16:27:29",-0.505,-0.60923076923076924]
[6,29,2018,16,28,19,-0.36,-0.36,"2018-06-29T16:28:19",-0.42499999999999999,{"$f":"AVERAGE(G11512:G11537)","v":-0.55499999999999994}]
[6,29,2018,16,29,19,-0.27,-0.27,"2018-06-29T16:29:19",-0.28499999999999998,-0.45923076923076928]
[6,29,2018,16,29,59,-0.51,-0.51,"2018-06-29T16:29:59",-0.32,-0.42923076923076925]
[6,29,2018,16,30,49,-0.24,-0.24,"2018-06-29T16:30:49",-0.4200000000000001,-0.39461538461538459]
[6,29,2018,16,31,49,-0.48,-0.48,"2018-06-29T16:31:49",-0.36000000000000004,-0.36115384615384616]
[6,29,2018,16,32,39,-0.48,-0.48,"2018-06-29T16:32:39",-0.47500000000000003,-0.36923076923076931]
[6,29,2018,16,32,49,-0.48,-0.48,"2018-06-29T16:32:49",-0.47500000000000003,-0.37384615384615394]
[6,29,2018,16,33,39,-0.69000000000000006,-0.69000000000000006,"2018-06-29T16:33:39",-0.65,-0.45346153846153847]
[6,29,2018,16,34,29,-0.51,-0.51,"2018-06-29T16:34:29",-0.625,-0.49846153846153851]
[6,29,2018,16,35,29,-0.84000000000000008,-0.84000000000000008,"2018-06-29T16:35:29",-0.67499999999999993,-0.57807692307692315]
[6,29,2018,16,36,19,-0.81,-0.81,"2018-06-29T16:36:19",-0.84500000000000008,-0.6611538461538462]
[6,29,2018,16,37,19,-1.08,-1.08,"2018-06-29T16:37:19",-1.03,-0.7811538461538462]
[6,29,2018,16,38,9,-1.02,-1.02,"2018-06-29T16:38:09",-1,-0.83769230769230763]
[6,29,2018,16,38,59,-1.02,-1.02,"2018-06-29T16:38:59",-1.0199999999999998,{"$f":"AVERAGE(G11576:G11601)","v":-0.91730769230769227}]
[6,29,2018,16,39,59,-0.75,-0.75,"2018-06-29T16:39:59",-0.89500000000000002,-0.95423076923076899]
[6,29,2018,16,40,49,-0.78,-0.78,"2018-06-29T16:40:49",-0.78500000000000003,-0.94615384615384612]
[6,29,2018,16,41,39,-0.42000000000000004,-0.42000000000000004,"2018-06-29T16:41:39",-0.61,-0.8550000000000002]
[6,29,2018,16,42,39,-0.54,-0.54,"2018-06-29T16:42:39",-0.56000000000000005,-0.75576923076923086]
[6,29,2018,16,42,49,-0.54,-0.54,"2018-06-29T16:42:49",-0.57000000000000006,-0.73615384615384616]
[6,29,2018,16,43,29,-0.75,-0.75,"2018-06-29T16:43:29",-0.63500000000000012,-0.6842307692307692]
[6,29,2018,16,44,19,-0.89999999999999991,-0.89999999999999991,"2018-06-29T16:44:19",-0.79499999999999993,-0.67269230769230781]
[6,29,2018,16,45,9,-1.1400000000000001,-1.1400000000000001,"2018-06-29T16:45:09",-1.03,-0.72346153846153838]
[6,29,2018,16,46,9,-1.08,-1.08,"2018-06-29T16:46:09",-1.095,-0.84692307692307678]
[6,29,2018,16,46,59,-1.1099999999999999,-1.1099999999999999,"2018-06-29T16:46:59",-1.0799999999999998,-0.943846153846154]
[6,29,2018,16,47,49,-0.78,-0.78,"2018-06-29T16:47:49",-0.96999999999999986,-0.99923076923076937]
[6,29,2018,16,48,49,-0.44999999999999996,-0.44999999999999996,"2018-06-29T16:48:49",-0.59,-0.943846153846154]
[6,29,2018,16,49,39,-0.33,-0.33,"2018-06-29T16:49:39",-0.38999999999999996,{"$f":"AVERAGE(G11640:G11665)","v":-0.80538461538461525}]
[6,29,2018,16,50,39,-0.36,-0.36,"2018-06-29T16:50:39",-0.44999999999999996,-0.66115384615384609]
[6,29,2018,16,51,29,-0.48,-0.48,"2018-06-29T16:51:29",-0.435,-0.53538461538461535]
[6,29,2018,16,52,19,-0.51,-0.51,"2018-06-29T16:52:19",-0.52499999999999991,-0.48000000000000004]
[6,29,2018,16,53,19,-0.21000000000000002,-0.21000000000000002,"2018-06-29T16:53:19",-0.30499999999999999,-0.41884615384615392]
[6,29,2018,16,54,9,-0.44999999999999996,-0.44999999999999996,"2018-06-29T16:54:09",-0.34500000000000003,-0.41653846153846152]
[6,29,2018,16,54,19,-0.33,-0.33,"2018-06-29T16:54:19",-0.36499999999999999,-0.40961538461538455]
[6,29,2018,16,55,9,-0.39,-0.39,"2018-06-29T16:55:09",-0.46,-0.42]
[6,29,2018,16,55,59,-0.63,-0.63,"2018-06-29T16:55:59",-0.57499999999999996,-0.44769230769230778]
[6,29,2018,16,56,59,-1.0499999999999998,-1.0499999999999998,"2018-06-29T16:56:59",{"$f":"AVERAGE(G11704:G11709)","v":-0.8849999999999999},-0.53884615384615386]
[6,29,2018,16,57,59,-0.96,-0.96,"2018-06-29T16:57:59",-0.94499999999999995,-0.69461538461538475]
[6,29,2018,16,58,29,-0.81,-0.81,"2018-06-29T16:58:29",-0.90999999999999981,-0.7465384615384616]
[6,29,2018,16,59,29,-0.92999999999999994,-0.92999999999999994,"2018-06-29T16:59:29",-0.9049999999999998,-0.84923076923076934]
[6,29,2018,17,0,19,-0.54,-0.54,"2018-06-29T17:00:19",-0.68,{"$f":"AVERAGE(G11704:G11729)","v":-0.85269230769230753}]
[6,29,2018,17,1,19,-0.57000000000000006,-0.57000000000000006,"2018-06-29T17:01:19",-0.61,-0.78923076923076918]
[6,29,2018,17,2,9,-0.60000000000000009,-0.60000000000000009,"2018-06-29T17:02:09",-0.48000000000000004,-0.69692307692307709]
[6,29,2018,17,2,59,-0.48,-0.48,"2018-06-29T17:02:59",-0.57999999999999996,-0.63692307692307704]
[6,29,2018,17,3,59,-0.51,-0.51,"2018-06-29T17:03:59",-0.56999999999999995,-0.56307692307692314]
[6,29,2018,17,4,49,-0.21000000000000002,-0.21000000000000002,"2018-06-29T17:04:49",-0.41000000000000009,-0.52730769230769237]
[6,29,2018,17,4,59,-0.33,-0.33,"2018-06-29T17:04:59",-0.38000000000000006,-0.51807692307692321]
[6,29,2018,17,5,49,-0.21000000000000002,-0.21000000000000002,"2018-06-29T17:05:49",-0.30499999999999999,-0.45923076923076928]
[6,29,2018,17,6,39,-0.27,-0.27,"2018-06-29T17:06:39",-0.22500000000000001,-0.40730769230769232]
[6,29,2018,17,7,39,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:07:39",{"$f":"AVERAGE(G11768:G11773)","v":-0.37999999999999995},-0.36461538461538462]
[6,29,2018,17,8,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T17:08:29",-0.55500000000000005,-0.36230769230769233]
[6,29,2018,17,9,19,-0.75,-0.75,"2018-06-29T17:09:19",-0.6150000000000001,-0.42115384615384621]
[6,29,2018,17,10,19,-0.66,-0.66,"2018-06-29T17:10:19",-0.69,-0.51346153846153864]
[6,29,2018,17,11,9,-0.63,-0.63,"2018-06-29T17:11:09",-0.66499999999999992,-0.59538461538461551]
[6,29,2018,17,12,9,-0.54,-0.54,"2018-06-29T17:12:09",-0.56999999999999995,-0.63576923076923086]
[6,29,2018,17,12,49,-0.72,-0.72,"2018-06-29T17:12:49",-0.69,-0.6565384615384614]
[6,29,2018,17,13,39,-0.69000000000000006,-0.69000000000000006,"2018-06-29T17:13:39",-0.67,-0.66346153846153855]
[6,29,2018,17,14,39,-0.60000000000000009,-0.60000000000000009,"2018-06-29T17:14:39",-0.62000000000000011,-0.64730769230769247]
[6,29,2018,17,15,29,-0.27,-0.27,"2018-06-29T17:15:29",-0.45500000000000002,-0.60115384615384615]
[6,29,2018,17,16,19,-0.48,-0.48,"2018-06-29T17:16:19",-0.38999999999999996,-0.57000000000000006]
[6,29,2018,17,16,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:16:29",-0.41500000000000004,-0.56538461538461537]
[6,29,2018,17,17,19,-0.21000000000000002,-0.21000000000000002,"2018-06-29T17:17:19",-0.32,-0.48000000000000004]
[6,29,2018,17,18,19,-0.27,-0.27,"2018-06-29T17:18:19",{"$f":"AVERAGE(G11832:G11837)","v":-0.19000000000000003},-0.37153846153846171]
[6,29,2018,17,19,9,-0.30000000000000004,-0.30000000000000004,"2018-06-29T17:19:09",-0.39500000000000002,-0.3403846153846154]
[6,29,2018,17,19,59,-0.63,-0.63,"2018-06-29T17:19:59",-0.40500000000000003,-0.34730769230769237]
[6,29,2018,17,20,59,-0.51,-0.51,"2018-06-29T17:20:59",-0.59500000000000008,-0.38653846153846155]
[6,29,2018,17,21,49,-0.36,-0.36,"2018-06-29T17:21:49",-0.36499999999999999,-0.39923076923076917]
[6,29,2018,17,22,49,-0.78,-0.78,"2018-06-29T17:22:49",-0.69000000000000006,-0.50884615384615384]
[6,29,2018,17,23,39,-0.69000000000000006,-0.69000000000000006,"2018-06-29T17:23:39",-0.76000000000000012,-0.57807692307692293]
[6,29,2018,17,24,29,-0.54,-0.54,"2018-06-29T17:24:29",-0.65,-0.60346153846153849]
[6,29,2018,17,25,29,-0.51,-0.51,"2018-06-29T17:25:29",-0.56500000000000006,-0.60692307692307701]
[6,29,2018,17,26,19,-0.48,-0.48,"2018-06-29T17:26:19",-0.53,-0.63923076923076938]
[6,29,2018,17,26,29,-0.54,-0.54,"2018-06-29T17:26:29",-0.53500000000000003,-0.6346153846153848]
[6,29,2018,17,26,39,-0.51,-0.51,"2018-06-29T17:26:39",-0.52500000000000002,-0.62884615384615405]
[6,29,2018,17,26,49,-0.44999999999999996,-0.44999999999999996,"2018-06-29T17:26:49",-0.505,-0.61961538461538468]
[6,29,2018,17,26,59,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:26:59",-0.49000000000000005,-0.60576923076923073]
[6,29,2018,17,27,9,-0.36,-0.36,"2018-06-29T17:27:09",-0.45999999999999996,-0.58961538461538465]
[6,29,2018,17,27,19,-0.36,-0.36,"2018-06-29T17:27:19",-0.43999999999999995,-0.5723076923076923]
[6,29,2018,17,27,29,-0.21000000000000002,-0.21000000000000002,"2018-06-29T17:27:29",-0.38499999999999995,-0.54807692307692313]
[6,29,2018,17,27,39,-0.24,-0.24,"2018-06-29T17:27:39",-0.34,-0.52846153846153843]
[6,29,2018,17,27,49,-0.24,-0.24,"2018-06-29T17:27:49",-0.30499999999999999,-0.51115384615384607]
[6,29,2018,17,27,59,-0.24,-0.24,"2018-06-29T17:27:59",-0.27499999999999997,-0.49384615384615377]
[6,29,2018,17,28,9,-0.21000000000000002,-0.21000000000000002,"2018-06-29T17:28:09",-0.25,-0.47538461538461541]
[6,29,2018,17,28,19,-0.18,-0.18,{"$f":"DATE(C11897,A11897,B11897)+TIME(D11897,E11897,F11897)","v":"2018-06-29T17:28:19"},-0.21999999999999997,-0.45576923076923076]
[6,29,2018,17,28,29,-0.12,-0.12,"2018-06-29T17:28:29",-0.20499999999999999,-0.43269230769230771]
[6,29,2018,17,28,39,-0.09,-0.09,"2018-06-29T17:28:39",-0.17999999999999997,-0.41423076923076929]
[6,29,2018,17,28,49,-0.15000000000000002,-0.15000000000000002,"2018-06-29T17:28:49",-0.16500000000000001,-0.39923076923076928]
[6,29,2018,17,28,59,-0.12,-0.12,"2018-06-29T17:28:59",{"$f":"AVERAGE(G11896:G11901)","v":-0.14499999999999999},-0.38076923076923086]
[6,29,2018,17,29,9,-0.09,-0.09,"2018-06-29T17:29:09",-0.125,-0.36346153846153845]
[6,29,2018,17,29,19,-0.09,-0.09,"2018-06-29T17:29:19",-0.10999999999999999,-0.3438461538461538]
[6,29,2018,17,29,29,-0.18,-0.18,"2018-06-29T17:29:29",-0.12,-0.3288461538461539]
[6,29,2018,17,29,39,-0.15000000000000002,-0.15000000000000002,"2018-06-29T17:29:39",-0.12999999999999998,-0.31269230769230771]
[6,29,2018,17,29,49,-0.18,-0.18,"2018-06-29T17:29:49",-0.13500000000000001,-0.30000000000000004]
[6,29,2018,17,29,59,-0.15000000000000002,-0.15000000000000002,"2018-06-29T17:29:59",-0.13999999999999999,-0.28384615384615391]
[6,29,2018,17,30,9,-0.21000000000000002,-0.21000000000000002,"2018-06-29T17:30:09",-0.16000000000000003,-0.27]
[6,29,2018,17,30,19,-0.24,-0.24,"2018-06-29T17:30:19",-0.18500000000000003,-0.25961538461538464]
[6,29,2018,17,30,29,-0.27,-0.27,"2018-06-29T17:30:29",-0.20000000000000004,-0.24923076923076926]
[6,29,2018,17,30,39,-0.33,-0.33,"2018-06-29T17:30:39",-0.23,-0.24346153846153845]
[6,29,2018,17,30,49,-0.36,-0.36,"2018-06-29T17:30:49",-0.26,-0.23653846153846159]
[6,29,2018,17,30,59,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:30:59",-0.30499999999999999,-0.23307692307692313]
[6,29,2018,17,31,9,-0.51,-0.51,"2018-06-29T17:31:09",-0.35499999999999998,-0.23538461538461539]
[6,29,2018,17,31,19,-0.44999999999999996,-0.44999999999999996,"2018-06-29T17:31:19",-0.38999999999999996,-0.23653846153846156]
[6,29,2018,17,31,29,-0.39,-0.39,"2018-06-29T17:31:29",-0.41,-0.23769230769230767]
[6,29,2018,17,31,39,-0.36,-0.36,"2018-06-29T17:31:39",-0.41499999999999998,-0.2376923076923077]
[6,29,2018,17,31,49,-0.44999999999999996,-0.44999999999999996,"2018-06-29T17:31:49",-0.43,-0.24692307692307697]
[6,29,2018,17,31,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T17:31:59",-0.43500000000000005,-0.255]
[6,29,2018,17,32,9,-0.60000000000000009,-0.60000000000000009,"2018-06-29T17:32:09",-0.44999999999999996,-0.26884615384615385]
[6,29,2018,17,32,19,-0.69000000000000006,-0.69000000000000006,"2018-06-29T17:32:19",-0.49,{"$f":"AVERAGE(G11896:G11921)","v":-0.28615384615384615}]
[6,29,2018,17,32,29,-0.78,-0.78,"2018-06-29T17:32:29",-0.55500000000000005,-0.30807692307692314]
[6,29,2018,17,32,39,-0.66,-0.66,"2018-06-29T17:32:39",-0.60499999999999998,-0.32653846153846161]
[6,29,2018,17,32,49,-0.66,-0.66,"2018-06-29T17:32:49",-0.64000000000000012,-0.34730769230769237]
[6,29,2018,17,32,59,-0.60000000000000009,-0.60000000000000009,"2018-06-29T17:32:59",-0.66500000000000015,-0.36692307692307696]
[6,29,2018,17,33,9,-0.57000000000000006,-0.57000000000000006,"2018-06-29T17:33:09",-0.66000000000000014,-0.38307692307692309]
[6,29,2018,17,33,19,-0.60000000000000009,-0.60000000000000009,"2018-06-29T17:33:19",-0.64500000000000013,-0.40153846153846157]
[6,29,2018,17,33,29,-0.60000000000000009,-0.60000000000000009,"2018-06-29T17:33:29",-0.6150000000000001,-0.42115384615384621]
[6,29,2018,17,33,39,-0.63,-0.63,"2018-06-29T17:33:39",-0.6100000000000001,-0.44192307692307697]
[6,29,2018,17,33,49,-0.57000000000000006,-0.57000000000000006,"2018-06-29T17:33:49",-0.59500000000000008,-0.45692307692307704]
[6,29,2018,17,33,59,-0.60000000000000009,-0.60000000000000009,"2018-06-29T17:33:59",-0.59500000000000008,-0.47423076923076929]
[6,29,2018,17,34,9,-0.57000000000000006,-0.57000000000000006,"2018-06-29T17:34:09",-0.59500000000000008,-0.4892307692307693]
[6,29,2018,17,34,19,-0.63,-0.63,"2018-06-29T17:34:19",-0.60000000000000009,-0.50769230769230778]
[6,29,2018,17,34,29,-0.63,-0.63,"2018-06-29T17:34:29",-0.60499999999999998,-0.52384615384615396]
[6,29,2018,17,34,39,-0.63,-0.63,"2018-06-29T17:34:39",-0.60499999999999998,-0.53884615384615397]
[6,29,2018,17,34,49,-0.63,-0.63,"2018-06-29T17:34:49",-0.61499999999999999,-0.55269230769230782]
[6,29,2018,17,34,59,-0.75,-0.75,"2018-06-29T17:34:59",-0.64,-0.568846153846154]
[6,29,2018,17,35,9,-0.66,-0.66,"2018-06-29T17:35:09",-0.65500000000000003,-0.58038461538461561]
[6,29,2018,17,35,19,-0.78,-0.78,"2018-06-29T17:35:19",-0.68,-0.59423076923076945]
[6,29,2018,17,35,29,-0.66,-0.66,"2018-06-29T17:35:29",-0.68500000000000005,-0.60000000000000009]
[6,29,2018,17,35,39,-0.57000000000000006,-0.57000000000000006,"2018-06-29T17:35:39",-0.67500000000000016,-0.60461538461538478]
[6,29,2018,17,35,49,-0.57000000000000006,-0.57000000000000006,"2018-06-29T17:35:49",-0.66500000000000015,-0.61153846153846159]
[6,29,2018,17,35,59,-0.57000000000000006,-0.57000000000000006,"2018-06-29T17:35:59",-0.63500000000000012,-0.61961538461538468]
[6,29,2018,17,36,9,-0.48,-0.48,"2018-06-29T17:36:09",-0.60500000000000009,-0.62076923076923096]
[6,29,2018,17,36,19,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:36:19",-0.54500000000000004,-0.6196153846153849]
[6,29,2018,17,36,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:36:29",-0.505,-0.61269230769230787]
[6,29,2018,17,36,39,-0.36,-0.36,"2018-06-29T17:36:39",-0.47,-0.60000000000000009]
[6,29,2018,17,36,49,-0.51,-0.51,"2018-06-29T17:36:49",-0.45999999999999996,-0.58961538461538465]
[6,29,2018,17,36,59,-0.33,-0.33,"2018-06-29T17:36:59",-0.4200000000000001,-0.57692307692307687]
[6,29,2018,17,37,9,-0.48,-0.48,"2018-06-29T17:37:09",-0.42,-0.57000000000000006]
[6,29,2018,17,37,19,-0.30000000000000004,-0.30000000000000004,"2018-06-29T17:37:19",-0.40000000000000008,-0.55846153846153856]
[6,29,2018,17,37,29,-0.27,-0.27,"2018-06-29T17:37:29",-0.375,-0.54692307692307696]
[6,29,2018,17,37,39,-0.24,-0.24,"2018-06-29T17:37:39",-0.35499999999999998,-0.53307692307692311]
[6,29,2018,17,37,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T17:37:49",-0.32,-0.52153846153846162]
[6,29,2018,17,37,59,-0.24,-0.24,"2018-06-29T17:37:59",-0.30499999999999999,-0.5065384615384616]
[6,29,2018,17,38,9,-0.24,-0.24,"2018-06-29T17:38:09",-0.26500000000000001,-0.49384615384615393]
[6,29,2018,17,38,19,-0.18,-0.18,"2018-06-29T17:38:19",-0.245,-0.47769230769230775]
[6,29,2018,17,38,29,-0.24,-0.24,"2018-06-29T17:38:29",-0.24,-0.46500000000000008]
[6,29,2018,17,38,39,-0.18,-0.18,"2018-06-29T17:38:39",-0.22999999999999998,-0.44769230769230778]
[6,29,2018,17,38,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T17:38:49",-0.22999999999999998,-0.43500000000000016]
[6,29,2018,17,38,59,-0.33,-0.33,{"$f":"DATE(C11961,A11961,B11961)+TIME(D11961,E11961,F11961)","v":"2018-06-29T17:38:59"},-0.245,-0.42346153846153861]
[6,29,2018,17,39,9,-0.24,-0.24,"2018-06-29T17:39:09",-0.245,-0.40846153846153854]
[6,29,2018,17,39,19,-0.18,-0.18,"2018-06-29T17:39:19",-0.245,-0.38653846153846155]
[6,29,2018,17,39,29,-0.18,-0.18,"2018-06-29T17:39:29",-0.23499999999999999,-0.36807692307692308]
[6,29,2018,17,39,39,-0.21000000000000002,-0.21000000000000002,"2018-06-29T17:39:39",{"$f":"AVERAGE(G11960:G11965)","v":-0.24},-0.34615384615384615]
[6,29,2018,17,39,49,-0.15000000000000002,-0.15000000000000002,"2018-06-29T17:39:49",-0.215,-0.32653846153846161]
[6,29,2018,17,39,59,-0.36,-0.36,"2018-06-29T17:39:59",-0.22,-0.31846153846153852]
[6,29,2018,17,40,9,-0.09,-0.09,"2018-06-29T17:40:09",-0.19500000000000003,-0.30000000000000004]
[6,29,2018,17,40,19,-0.18,-0.18,"2018-06-29T17:40:19",-0.19499999999999998,-0.28500000000000003]
[6,29,2018,17,40,29,-0.24,-0.24,"2018-06-29T17:40:29",-0.20499999999999999,-0.27576923076923077]
[6,29,2018,17,40,39,-0.33,-0.33,"2018-06-29T17:40:39",-0.22500000000000001,-0.27230769230769231]
[6,29,2018,17,40,49,-0.33,-0.33,"2018-06-29T17:40:49",-0.255,-0.2688461538461539]
[6,29,2018,17,40,59,-0.39,-0.39,"2018-06-29T17:40:59",-0.26,-0.27]
[6,29,2018,17,41,9,-0.39,-0.39,"2018-06-29T17:41:09",-0.31000000000000005,-0.26538461538461539]
[6,29,2018,17,41,19,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:41:19",-0.35000000000000003,-0.2688461538461539]
[6,29,2018,17,41,29,-0.39,-0.39,"2018-06-29T17:41:29",-0.375,-0.26538461538461539]
[6,29,2018,17,41,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T17:41:39",-0.36999999999999994,-0.26538461538461533]
[6,29,2018,17,41,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T17:41:49",-0.36500000000000005,-0.2665384615384615]
[6,29,2018,17,41,59,-0.36,-0.36,"2018-06-29T17:41:59",-0.36000000000000004,-0.27115384615384613]
[6,29,2018,17,42,9,-0.33,-0.33,"2018-06-29T17:42:09",-0.35000000000000003,-0.27230769230769225]
[6,29,2018,17,42,19,-0.33,-0.33,"2018-06-29T17:42:19",-0.33500000000000002,-0.27576923076923071]
[6,29,2018,17,42,29,-0.33,-0.33,"2018-06-29T17:42:29",-0.32500000000000001,-0.27923076923076917]
[6,29,2018,17,42,39,-0.44999999999999996,-0.44999999999999996,"2018-06-29T17:42:39",-0.35000000000000003,-0.28961538461538461]
[6,29,2018,17,42,49,-0.57000000000000006,-0.57000000000000006,"2018-06-29T17:42:49",-0.39500000000000002,-0.30230769230769233]
[6,29,2018,17,42,59,-0.54,-0.54,"2018-06-29T17:42:59",-0.42499999999999999,{"$f":"AVERAGE(G11960:G11985)","v":-0.31615384615384617}]
[6,29,2018,17,43,9,-0.48,-0.48,"2018-06-29T17:43:09",-0.44999999999999996,-0.32307692307692309]
[6,29,2018,17,43,19,-0.54,-0.54,"2018-06-29T17:43:19",-0.48500000000000004,-0.33115384615384613]
[6,29,2018,17,43,29,-0.66,-0.66,"2018-06-29T17:43:29",-0.54,-0.34730769230769237]
[6,29,2018,17,43,39,-0.72,-0.72,"2018-06-29T17:43:39",-0.58499999999999996,-0.36807692307692313]
[6,29,2018,17,43,49,-0.69000000000000006,-0.69000000000000006,"2018-06-29T17:43:49",-0.60500000000000009,-0.38769230769230778]
[6,29,2018,17,43,59,-0.72,-0.72,"2018-06-29T17:43:59",-0.63500000000000012,-0.40730769230769237]
[6,29,2018,17,44,9,-0.75,-0.75,"2018-06-29T17:44:09",-0.68,-0.43038461538461542]
[6,29,2018,17,44,19,-0.63,-0.63,"2018-06-29T17:44:19",-0.69499999999999995,-0.4407692307692308]
[6,29,2018,17,44,29,-0.54,-0.54,"2018-06-29T17:44:29",-0.67499999999999993,-0.4580769230769231]
[6,29,2018,17,44,39,-0.60000000000000009,-0.60000000000000009,"2018-06-29T17:44:39",-0.65500000000000003,-0.47423076923076923]
[6,29,2018,17,44,49,-0.57000000000000006,-0.57000000000000006,"2018-06-29T17:44:49",-0.63500000000000012,-0.48692307692307701]
[6,29,2018,17,44,59,-0.66,-0.66,"2018-06-29T17:44:59",-0.625,-0.49961538461538463]
[6,29,2018,17,45,9,-0.81,-0.81,"2018-06-29T17:45:09",-0.63500000000000001,-0.51807692307692321]
[6,29,2018,17,45,19,-0.78,-0.78,"2018-06-29T17:45:19",-0.66,-0.53307692307692311]
[6,29,2018,17,45,29,-0.72,-0.72,"2018-06-29T17:45:29",-0.69,-0.54576923076923078]
[6,29,2018,17,45,39,-0.69000000000000006,-0.69000000000000006,"2018-06-29T17:45:39",-0.70500000000000007,-0.55615384615384622]
[6,29,2018,17,45,49,-0.66,-0.66,"2018-06-29T17:45:49",-0.71999999999999986,-0.56653846153846166]
[6,29,2018,17,45,59,-0.57000000000000006,-0.57000000000000006,"2018-06-29T17:45:59",-0.70500000000000007,-0.57692307692307698]
[6,29,2018,17,46,9,-0.48,-0.48,"2018-06-29T17:46:09",-0.65,-0.5838461538461539]
[6,29,2018,17,46,19,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:46:19",-0.59000000000000008,-0.58615384615384614]
[6,29,2018,17,46,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:46:29",-0.54,-0.58961538461538465]
[6,29,2018,17,46,39,-0.44999999999999996,-0.44999999999999996,"2018-06-29T17:46:39",-0.5,-0.59423076923076923]
[6,29,2018,17,46,49,-0.51,-0.51,"2018-06-29T17:46:49",-0.47499999999999992,-0.60115384615384615]
[6,29,2018,17,46,59,-0.51,-0.51,"2018-06-29T17:46:59",-0.46500000000000002,-0.60346153846153849]
[6,29,2018,17,47,9,-0.54,-0.54,"2018-06-29T17:47:09",-0.47500000000000003,-0.60230769230769232]
[6,29,2018,17,47,19,-0.54,-0.54,"2018-06-29T17:47:19",-0.49499999999999994,-0.60230769230769232]
[6,29,2018,17,47,29,-0.48,-0.48,"2018-06-29T17:47:29",-0.505,-0.60230769230769232]
[6,29,2018,17,47,39,-0.48,-0.48,"2018-06-29T17:47:39",-0.51,-0.60000000000000009]
[6,29,2018,17,47,49,-0.39,-0.39,"2018-06-29T17:47:49",-0.49000000000000005,-0.58961538461538465]
[6,29,2018,17,47,59,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:47:59",-0.47500000000000003,-0.57807692307692304]
[6,29,2018,17,48,9,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:48:09",-0.45500000000000002,-0.56769230769230772]
[6,29,2018,17,48,19,-0.39,-0.39,"2018-06-29T17:48:19",-0.43,-0.55499999999999994]
[6,29,2018,17,48,29,-0.54,-0.54,"2018-06-29T17:48:29",-0.44,-0.54692307692307685]
[6,29,2018,17,48,39,-0.57000000000000006,-0.57000000000000006,"2018-06-29T17:48:39",-0.45500000000000007,-0.54461538461538461]
[6,29,2018,17,48,49,-0.75,-0.75,"2018-06-29T17:48:49",-0.51500000000000001,-0.5526923076923077]
[6,29,2018,17,48,59,-0.75,-0.75,"2018-06-29T17:48:59",-0.56999999999999995,-0.55846153846153856]
[6,29,2018,17,49,9,-0.78,-0.78,"2018-06-29T17:49:09",-0.63,-0.56653846153846144]
[6,29,2018,17,49,19,-0.81,-0.81,"2018-06-29T17:49:19",-0.70000000000000018,-0.57230769230769241]
[6,29,2018,17,49,29,-0.72,-0.72,"2018-06-29T17:49:29",-0.73000000000000009,-0.56884615384615389]
[6,29,2018,17,49,39,-0.69000000000000006,-0.69000000000000006,{"$f":"DATE(C12025,A12025,B12025)+TIME(D12025,E12025,F12025)","v":"2018-06-29T17:49:39"},-0.75000000000000011,-0.56538461538461549]
[6,29,2018,17,49,49,-0.69000000000000006,-0.69000000000000006,"2018-06-29T17:49:49",-0.73999999999999988,-0.5642307692307692]
[6,29,2018,17,49,59,-0.75,-0.75,"2018-06-29T17:49:59",-0.73999999999999988,-0.56653846153846144]
[6,29,2018,17,50,9,-0.86999999999999988,-0.86999999999999988,"2018-06-29T17:50:09",-0.755,-0.57461538461538453]
[6,29,2018,17,50,19,-0.81,-0.81,"2018-06-29T17:50:19",{"$f":"AVERAGE(G12024:G12029)","v":-0.75499999999999989},-0.58384615384615379]
[6,29,2018,17,50,29,-0.63,-0.63,"2018-06-29T17:50:29",-0.7400000000000001,-0.58961538461538454]
[6,29,2018,17,50,39,-0.51,-0.51,"2018-06-29T17:50:39",-0.71,-0.59307692307692306]
[6,29,2018,17,50,49,-0.54,-0.54,"2018-06-29T17:50:49",-0.68499999999999994,-0.59769230769230763]
[6,29,2018,17,50,59,-0.60000000000000009,-0.60000000000000009,"2018-06-29T17:50:59",-0.66,-0.60346153846153849]
[6,29,2018,17,51,9,-0.66,-0.66,"2018-06-29T17:51:09",-0.62500000000000011,-0.60923076923076924]
[6,29,2018,17,51,19,-0.57000000000000006,-0.57000000000000006,"2018-06-29T17:51:19",-0.58500000000000008,-0.61153846153846159]
[6,29,2018,17,51,29,-0.63,-0.63,"2018-06-29T17:51:29",-0.58499999999999996,-0.6150000000000001]
[6,29,2018,17,51,39,-0.54,-0.54,"2018-06-29T17:51:39",-0.59,-0.6150000000000001]
[6,29,2018,17,51,49,-0.54,-0.54,"2018-06-29T17:51:49",-0.59000000000000008,-0.61730769230769234]
[6,29,2018,17,51,59,-0.54,-0.54,"2018-06-29T17:51:59",-0.57999999999999996,-0.61961538461538457]
[6,29,2018,17,52,9,-0.51,-0.51,"2018-06-29T17:52:09",-0.55500000000000005,-0.62423076923076926]
[6,29,2018,17,52,19,-0.44999999999999996,-0.44999999999999996,"2018-06-29T17:52:19",-0.53500000000000003,-0.62538461538461543]
[6,29,2018,17,52,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:52:29",-0.5,-0.62538461538461532]
[6,29,2018,17,52,39,-0.24,-0.24,"2018-06-29T17:52:39",-0.45,-0.61961538461538457]
[6,29,2018,17,52,49,-0.21000000000000002,-0.21000000000000002,"2018-06-29T17:52:49",-0.39500000000000002,-0.6069230769230769]
[6,29,2018,17,52,59,-0.24,-0.24,"2018-06-29T17:52:59",-0.34499999999999997,-0.59423076923076923]
[6,29,2018,17,53,9,-0.33,-0.33,"2018-06-29T17:53:09",-0.315,-0.57807692307692304]
[6,29,2018,17,53,19,-0.36,-0.36,"2018-06-29T17:53:19",-0.30000000000000004,-0.56307692307692303]
[6,29,2018,17,53,29,-0.39,-0.39,"2018-06-29T17:53:29",-0.29499999999999998,-0.54807692307692302]
[6,29,2018,17,53,39,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:53:39",-0.32500000000000001,{"$f":"AVERAGE(G12024:G12049)","v":-0.533076923076923}]
[6,29,2018,17,53,49,-0.36,-0.36,"2018-06-29T17:53:49",-0.35000000000000003,-0.51923076923076927]
[6,29,2018,17,53,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T17:53:59",-0.38499999999999995,-0.5099999999999999]
[6,29,2018,17,54,9,-0.48,-0.48,"2018-06-29T17:54:09",-0.41,-0.50192307692307692]
[6,29,2018,17,54,19,-0.44999999999999996,-0.44999999999999996,"2018-06-29T17:54:19",-0.42499999999999999,-0.49038461538461536]
[6,29,2018,17,54,29,-0.48,-0.48,"2018-06-29T17:54:29",-0.44,-0.47538461538461535]
[6,29,2018,17,54,39,-0.44999999999999996,-0.44999999999999996,"2018-06-29T17:54:39",-0.44500000000000001,-0.46153846153846145]
[6,29,2018,17,54,49,-0.48,-0.48,"2018-06-29T17:54:49",-0.46499999999999991,-0.45576923076923076]
[6,29,2018,17,54,59,-0.36,-0.36,"2018-06-29T17:54:59",-0.44999999999999996,-0.44999999999999996]
[6,29,2018,17,55,9,-0.44999999999999996,-0.44999999999999996,"2018-06-29T17:55:09",-0.44500000000000001,-0.44653846153846144]
[6,29,2018,17,55,19,-0.51,-0.51,"2018-06-29T17:55:19",-0.4549999999999999,-0.44307692307692303]
[6,29,2018,17,55,29,-0.54,-0.54,"2018-06-29T17:55:29",-0.46500000000000002,-0.4384615384615384]
[6,29,2018,17,55,39,-0.54,-0.54,"2018-06-29T17:55:39",-0.48,-0.43730769230769223]
[6,29,2018,17,55,49,-0.51,-0.51,"2018-06-29T17:55:49",-0.48500000000000004,-0.4326923076923076]
[6,29,2018,17,55,59,-0.51,-0.51,"2018-06-29T17:55:59",-0.5099999999999999,-0.43153846153846148]
[6,29,2018,17,56,9,-0.51,-0.51,"2018-06-29T17:56:09",-0.52,-0.43038461538461537]
[6,29,2018,17,56,19,-0.44999999999999996,-0.44999999999999996,"2018-06-29T17:56:19",-0.51000000000000012,-0.42692307692307679]
[6,29,2018,17,56,29,-0.44999999999999996,-0.44999999999999996,"2018-06-29T17:56:29",-0.49500000000000011,-0.42461538461538451]
[6,29,2018,17,56,39,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:56:39",-0.47499999999999992,-0.42346153846153839]
[6,29,2018,17,56,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:56:49",-0.45999999999999996,-0.42346153846153839]
[6,29,2018,17,56,59,-0.48,-0.48,"2018-06-29T17:56:59",-0.45500000000000002,-0.4326923076923076]
[6,29,2018,17,57,9,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:57:09",-0.43999999999999995,-0.44076923076923069]
[6,29,2018,17,57,19,-0.36,-0.36,"2018-06-29T17:57:19",-0.42499999999999999,-0.44538461538461527]
[6,29,2018,17,57,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T17:57:29",-0.42,-0.44884615384615378]
[6,29,2018,17,57,39,-0.44999999999999996,-0.44999999999999996,"2018-06-29T17:57:39",-0.42499999999999999,-0.45230769230769219]
[6,29,2018,17,57,49,-0.44999999999999996,-0.44999999999999996,"2018-06-29T17:57:49",-0.43,-0.45461538461538448]
[6,29,2018,17,57,59,-0.39,-0.39,"2018-06-29T17:57:59",-0.41500000000000004,-0.45346153846153842]
[6,29,2018,17,58,9,-0.48,-0.48,"2018-06-29T17:58:09",-0.42499999999999999,-0.45807692307692299]
[6,29,2018,17,58,19,-0.48,-0.48,"2018-06-29T17:58:19",-0.44500000000000001,-0.45923076923076922]
[6,29,2018,17,58,29,-0.51,-0.51,"2018-06-29T17:58:29",-0.45999999999999996,-0.46038461538461534]
[6,29,2018,17,58,39,-0.48,-0.48,"2018-06-29T17:58:39",-0.46499999999999991,-0.46153846153846145]
[6,29,2018,17,58,49,-0.63,-0.63,"2018-06-29T17:58:49",-0.49499999999999994,-0.46730769230769237]
[6,29,2018,17,58,59,-0.57000000000000006,-0.57000000000000006,"2018-06-29T17:58:59",-0.52500000000000002,-0.471923076923077]
[6,29,2018,17,59,9,-0.60000000000000009,-0.60000000000000009,"2018-06-29T17:59:09",-0.54500000000000004,-0.47653846153846163]
[6,29,2018,17,59,19,-0.60000000000000009,-0.60000000000000009,"2018-06-29T17:59:19",-0.56500000000000006,-0.48576923076923079]
[6,29,2018,17,59,29,-0.24,-0.24,"2018-06-29T17:59:29",-0.52,-0.47769230769230775]
[6,29,2018,17,59,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T17:59:39",-0.49000000000000005,-0.46961538461538471]
[6,29,2018,17,59,49,-0.44999999999999996,-0.44999999999999996,"2018-06-29T17:59:49",-0.46000000000000013,-0.46615384615384625]
[6,29,2018,17,59,59,-0.36,-0.36,"2018-06-29T17:59:59",-0.42500000000000004,-0.45923076923076928]
[6,29,2018,18,0,9,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:00:09",-0.40000000000000008,-0.45692307692307688]
[6,29,2018,18,0,19,-0.33,-0.33,{"$f":"DATE(C12089,A12089,B12089)+TIME(D12089,E12089,F12089)","v":"2018-06-29T18:00:19"},-0.35499999999999998,-0.4499999999999999]
[6,29,2018,18,0,29,-0.36,-0.36,"2018-06-29T18:00:29",-0.375,-0.44423076923076921]
[6,29,2018,18,0,39,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:00:39",-0.39999999999999991,-0.44423076923076921]
[6,29,2018,18,0,49,-0.51,-0.51,"2018-06-29T18:00:49",-0.41,-0.44653846153846144]
[6,29,2018,18,0,59,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:00:59",{"$f":"AVERAGE(G12088:G12093)","v":-0.44500000000000001},-0.45230769230769224]
[6,29,2018,18,1,9,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:01:09",-0.47,-0.45923076923076916]
[6,29,2018,18,1,19,-0.66,-0.66,"2018-06-29T18:01:19",-0.52500000000000002,-0.46615384615384603]
[6,29,2018,18,1,29,-0.63,-0.63,"2018-06-29T18:01:29",-0.56999999999999995,-0.47423076923076923]
[6,29,2018,18,1,39,-0.63,-0.63,"2018-06-29T18:01:39",-0.6,-0.48461538461538467]
[6,29,2018,18,1,49,-0.63,-0.63,"2018-06-29T18:01:49",-0.62,-0.49269230769230771]
[6,29,2018,18,1,59,-0.75,-0.75,"2018-06-29T18:01:59",-0.65,-0.50423076923076937]
[6,29,2018,18,2,9,-0.69000000000000006,-0.69000000000000006,"2018-06-29T18:02:09",-0.66499999999999992,-0.51346153846153864]
[6,29,2018,18,2,19,-0.69000000000000006,-0.69000000000000006,"2018-06-29T18:02:19",-0.67,-0.52500000000000013]
[6,29,2018,18,2,29,-0.63,-0.63,"2018-06-29T18:02:29",-0.66999999999999993,-0.53076923076923088]
[6,29,2018,18,2,39,-0.54,-0.54,"2018-06-29T18:02:39",-0.65499999999999992,-0.53307692307692323]
[6,29,2018,18,2,49,-0.48,-0.48,"2018-06-29T18:02:49",-0.63,-0.53192307692307716]
[6,29,2018,18,2,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:02:59",-0.58000000000000007,-0.53076923076923088]
[6,29,2018,18,3,9,-0.48,-0.48,"2018-06-29T18:03:09",-0.54500000000000004,-0.52500000000000013]
[6,29,2018,18,3,19,-0.48,-0.48,"2018-06-29T18:03:19",-0.5099999999999999,-0.52153846153846162]
[6,29,2018,18,3,29,-0.48,-0.48,"2018-06-29T18:03:29",-0.48499999999999993,-0.51692307692307693]
[6,29,2018,18,3,39,-0.48,-0.48,"2018-06-29T18:03:39",-0.47500000000000003,-0.51230769230769235]
[6,29,2018,18,3,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T18:03:49",-0.46500000000000002,-0.51923076923076927]
[6,29,2018,18,3,59,-0.18,-0.18,"2018-06-29T18:03:59",-0.42,-0.5146153846153847]
[6,29,2018,18,4,9,-0.36,-0.36,"2018-06-29T18:04:09",-0.39999999999999997,-0.51115384615384618]
[6,29,2018,18,4,19,-0.33,-0.33,"2018-06-29T18:04:19",-0.375,{"$f":"AVERAGE(G12088:G12113)","v":-0.51}]
[6,29,2018,18,4,29,-0.30000000000000004,-0.30000000000000004,"2018-06-29T18:04:29",-0.34500000000000003,-0.50423076923076937]
[6,29,2018,18,4,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T18:04:39",-0.315,-0.5030769230769232]
[6,29,2018,18,4,49,-0.39,-0.39,"2018-06-29T18:04:49",-0.31000000000000005,-0.50423076923076937]
[6,29,2018,18,4,59,-0.39,-0.39,"2018-06-29T18:04:59",-0.34500000000000003,-0.50192307692307714]
[6,29,2018,18,5,9,-0.42000000000000004,-0.42000000000000004,"2018-06-29T18:05:09",-0.35500000000000004,-0.49846153846153857]
[6,29,2018,18,5,19,-0.39,-0.39,"2018-06-29T18:05:19",-0.36500000000000005,-0.49153846153846165]
[6,29,2018,18,5,29,-0.36,-0.36,"2018-06-29T18:05:29",-0.375,-0.48230769230769244]
[6,29,2018,18,5,39,-0.36,-0.36,"2018-06-29T18:05:39",-0.38500000000000001,-0.47076923076923083]
[6,29,2018,18,5,49,-0.36,-0.36,"2018-06-29T18:05:49",-0.37999999999999995,-0.46038461538461539]
[6,29,2018,18,5,59,-0.33,-0.33,"2018-06-29T18:05:59",-0.36999999999999994,-0.44884615384615389]
[6,29,2018,18,6,9,-0.42000000000000004,-0.42000000000000004,"2018-06-29T18:06:09",-0.36999999999999994,-0.4407692307692308]
[6,29,2018,18,6,19,-0.51,-0.51,"2018-06-29T18:06:19",-0.38999999999999996,-0.43153846153846148]
[6,29,2018,18,6,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:06:29",-0.42500000000000004,-0.42692307692307685]
[6,29,2018,18,6,39,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:06:39",-0.45999999999999996,-0.42230769230769227]
[6,29,2018,18,6,49,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:06:49",-0.50000000000000011,-0.4211538461538461]
[6,29,2018,18,6,59,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:06:59",-0.54500000000000004,-0.42346153846153844]
[6,29,2018,18,7,9,-0.63,-0.63,"2018-06-29T18:07:09",-0.57999999999999996,-0.42923076923076925]
[6,29,2018,18,7,19,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:07:19",-0.59500000000000008,-0.43499999999999994]
[6,29,2018,18,7,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:07:29",-0.59500000000000008,-0.43846153846153846]
[6,29,2018,18,7,39,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:07:39",-0.57500000000000007,-0.43730769230769234]
[6,29,2018,18,7,49,-0.39,-0.39,"2018-06-29T18:07:49",-0.54000000000000015,-0.43384615384615388]
[6,29,2018,18,7,59,-0.39,-0.39,"2018-06-29T18:07:59",-0.505,-0.43038461538461542]
[6,29,2018,18,8,9,-0.36,-0.36,"2018-06-29T18:08:09",-0.46,-0.42807692307692313]
[6,29,2018,18,8,19,-0.39,-0.39,"2018-06-29T18:08:19",-0.42500000000000004,-0.43615384615384623]
[6,29,2018,18,8,29,-0.33,-0.33,"2018-06-29T18:08:29",-0.38500000000000001,-0.43500000000000011]
[6,29,2018,18,8,39,-0.27,-0.27,"2018-06-29T18:08:39",-0.35500000000000004,-0.43269230769230776]
[6,29,2018,18,8,49,-0.33,-0.33,"2018-06-29T18:08:49",-0.34500000000000003,-0.43384615384615388]
[6,29,2018,18,8,59,-0.36,-0.36,"2018-06-29T18:08:59",-0.34,-0.43615384615384617]
[6,29,2018,18,9,9,-0.48,-0.48,"2018-06-29T18:09:09",-0.36000000000000004,-0.43961538461538469]
[6,29,2018,18,9,19,-0.42000000000000004,-0.42000000000000004,"2018-06-29T18:09:19",-0.36499999999999999,-0.4407692307692308]
[6,29,2018,18,9,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T18:09:29",-0.37999999999999995,-0.4407692307692308]
[6,29,2018,18,9,39,-0.36,-0.36,"2018-06-29T18:09:39",-0.39499999999999996,-0.43961538461538463]
[6,29,2018,18,9,49,-0.48,-0.48,"2018-06-29T18:09:49",-0.42,-0.44423076923076926]
[6,29,2018,18,9,59,-0.54,-0.54,"2018-06-29T18:09:59",-0.45,-0.45115384615384602]
[6,29,2018,18,10,9,-0.54,-0.54,"2018-06-29T18:10:09",-0.46,-0.4580769230769231]
[6,29,2018,18,10,19,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:10:19",-0.49,-0.46846153846153837]
[6,29,2018,18,10,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:10:29",-0.51500000000000001,-0.47423076923076923]
[6,29,2018,18,10,39,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:10:39",-0.55500000000000005,-0.47769230769230764]
[6,29,2018,18,10,49,-0.48,-0.48,"2018-06-29T18:10:49",-0.55500000000000005,-0.47423076923076918]
[6,29,2018,18,10,59,-0.44999999999999996,-0.44999999999999996,{"$f":"DATE(C12153,A12153,B12153)+TIME(D12153,E12153,F12153)","v":"2018-06-29T18:10:59"},-0.54,-0.46961538461538449]
[6,29,2018,18,11,9,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:11:09",-0.52500000000000002,-0.4638461538461538]
[6,29,2018,18,11,19,-0.54,-0.54,"2018-06-29T18:11:19",-0.51500000000000001,-0.46153846153846156]
[6,29,2018,18,11,29,-0.54,-0.54,"2018-06-29T18:11:29",-0.51,-0.45807692307692294]
[6,29,2018,18,11,39,-0.66,-0.66,"2018-06-29T18:11:39",{"$f":"AVERAGE(G12152:G12157)","v":-0.52},-0.46038461538461534]
[6,29,2018,18,11,49,-0.63,-0.63,"2018-06-29T18:11:49",-0.54500000000000004,-0.46269230769230768]
[6,29,2018,18,11,59,-0.69000000000000006,-0.69000000000000006,"2018-06-29T18:11:59",-0.58499999999999996,-0.47192307692307689]
[6,29,2018,18,12,9,-0.69000000000000006,-0.69000000000000006,"2018-06-29T18:12:09",-0.625,-0.48346153846153839]
[6,29,2018,18,12,19,-0.69000000000000006,-0.69000000000000006,"2018-06-29T18:12:19",-0.65,-0.49499999999999988]
[6,29,2018,18,12,29,-0.72,-0.72,"2018-06-29T18:12:29",-0.68,-0.50884615384615384]
[6,29,2018,18,12,39,-0.75,-0.75,"2018-06-29T18:12:39",-0.69499999999999995,-0.52269230769230757]
[6,29,2018,18,12,49,-0.72,-0.72,"2018-06-29T18:12:49",-0.71,-0.53769230769230769]
[6,29,2018,18,12,59,-0.69000000000000006,-0.69000000000000006,"2018-06-29T18:12:59",-0.71000000000000008,-0.55384615384615388]
[6,29,2018,18,13,9,-0.66,-0.66,"2018-06-29T18:13:09",-0.70499999999999996,-0.56653846153846166]
[6,29,2018,18,13,19,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:13:19",-0.69000000000000006,-0.57576923076923081]
[6,29,2018,18,13,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:13:29",-0.66500000000000004,-0.57923076923076933]
[6,29,2018,18,13,39,-0.54,-0.54,"2018-06-29T18:13:39",-0.63,-0.58384615384615379]
[6,29,2018,18,13,49,-0.51,-0.51,"2018-06-29T18:13:49",-0.59500000000000008,-0.58730769230769231]
[6,29,2018,18,13,59,-0.54,-0.54,"2018-06-29T18:13:59",-0.56999999999999995,-0.59423076923076934]
[6,29,2018,18,14,9,-0.48,-0.48,"2018-06-29T18:14:09",-0.54,-0.59423076923076934]
[6,29,2018,18,14,19,-0.48,-0.48,"2018-06-29T18:14:19",-0.52,-0.59192307692307711]
[6,29,2018,18,14,29,-0.48,-0.48,"2018-06-29T18:14:29",-0.505,-0.58961538461538487]
[6,29,2018,18,14,39,-0.54,-0.54,"2018-06-29T18:14:39",-0.505,-0.58730769230769242]
[6,29,2018,18,14,49,-0.48,-0.48,"2018-06-29T18:14:49",-0.5,-0.58384615384615401]
[6,29,2018,18,14,59,-0.54,-0.54,"2018-06-29T18:14:59",-0.5,{"$f":"AVERAGE(G12152:G12177)","v":-0.58153846153846156}]
[6,29,2018,18,15,9,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:15:09",-0.51500000000000001,-0.58500000000000008]
[6,29,2018,18,15,19,-0.51,-0.51,"2018-06-29T18:15:19",-0.52,-0.58730769230769231]
[6,29,2018,18,15,29,-0.51,-0.51,"2018-06-29T18:15:29",-0.52499999999999991,-0.58961538461538465]
[6,29,2018,18,15,39,-0.54,-0.54,"2018-06-29T18:15:39",-0.52500000000000002,-0.58961538461538465]
[6,29,2018,18,15,49,-0.54,-0.54,"2018-06-29T18:15:49",-0.53500000000000003,-0.58961538461538454]
[6,29,2018,18,15,59,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:15:59",-0.54,-0.58615384615384614]
[6,29,2018,18,16,9,-0.51,-0.51,"2018-06-29T18:16:09",-0.52999999999999992,-0.58153846153846156]
[6,29,2018,18,16,19,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:16:19",-0.52,-0.5723076923076923]
[6,29,2018,18,16,29,-0.54,-0.54,"2018-06-29T18:16:29",-0.52500000000000002,-0.56653846153846155]
[6,29,2018,18,16,39,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:16:39",-0.51000000000000012,-0.55730769230769228]
[6,29,2018,18,16,49,-0.42000000000000004,-0.42000000000000004,"2018-06-29T18:16:49",-0.49000000000000005,-0.54576923076923078]
[6,29,2018,18,16,59,-0.33,-0.33,"2018-06-29T18:16:59",-0.45,-0.5296153846153846]
[6,29,2018,18,17,9,-0.39,-0.39,"2018-06-29T18:17:09",-0.43,-0.51692307692307693]
[6,29,2018,18,17,19,-0.36,-0.36,"2018-06-29T18:17:19",-0.41500000000000004,-0.50423076923076926]
[6,29,2018,18,17,29,-0.33,-0.33,"2018-06-29T18:17:29",-0.37999999999999995,-0.49153846153846154]
[6,29,2018,18,17,39,-0.33,-0.33,"2018-06-29T18:17:39",-0.36000000000000004,-0.4811538461538461]
[6,29,2018,18,17,49,-0.33,-0.33,"2018-06-29T18:17:49",-0.34500000000000003,-0.471923076923077]
[6,29,2018,18,17,59,-0.39,-0.39,"2018-06-29T18:17:59",-0.35500000000000004,-0.46615384615384614]
[6,29,2018,18,18,9,-0.42000000000000004,-0.42000000000000004,"2018-06-29T18:18:09",-0.36000000000000004,-0.46269230769230774]
[6,29,2018,18,18,19,-0.48,-0.48,"2018-06-29T18:18:19",-0.37999999999999995,-0.46038461538461539]
[6,29,2018,18,18,29,-0.39,-0.39,"2018-06-29T18:18:29",-0.39000000000000007,-0.45692307692307704]
[6,29,2018,18,18,39,-0.30000000000000004,-0.30000000000000004,"2018-06-29T18:18:39",-0.38500000000000006,-0.45000000000000012]
[6,29,2018,18,18,49,-0.39,-0.39,"2018-06-29T18:18:49",-0.39500000000000002,-0.44653846153846166]
[6,29,2018,18,18,59,-0.39,-0.39,"2018-06-29T18:18:59",-0.39500000000000002,-0.44076923076923091]
[6,29,2018,18,19,9,-0.36,-0.36,"2018-06-29T18:19:09",-0.38500000000000001,-0.43615384615384628]
[6,29,2018,18,19,19,-0.39,-0.39,"2018-06-29T18:19:19",-0.37000000000000005,-0.43038461538461548]
[6,29,2018,18,19,29,-0.30000000000000004,-0.30000000000000004,"2018-06-29T18:19:29",-0.35499999999999998,-0.42000000000000015]
[6,29,2018,18,19,39,-0.42000000000000004,-0.42000000000000004,"2018-06-29T18:19:39",-0.37500000000000006,-0.41653846153846169]
[6,29,2018,18,19,49,-0.39,-0.39,"2018-06-29T18:19:49",-0.37500000000000006,-0.411923076923077]
[6,29,2018,18,19,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:19:59",-0.38500000000000006,-0.40846153846153843]
[6,29,2018,18,20,9,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:20:09",-0.39999999999999997,-0.40499999999999997]
[6,29,2018,18,20,19,-0.42000000000000004,-0.42000000000000004,"2018-06-29T18:20:19",-0.40499999999999997,-0.39923076923076917]
[6,29,2018,18,20,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T18:20:29",-0.42499999999999999,-0.39576923076923076]
[6,29,2018,18,20,39,-0.39,-0.39,"2018-06-29T18:20:39",-0.42,-0.39346153846153842]
[6,29,2018,18,20,49,-0.36,-0.36,"2018-06-29T18:20:49",-0.41499999999999998,-0.38653846153846144]
[6,29,2018,18,20,59,-0.42000000000000004,-0.42000000000000004,"2018-06-29T18:20:59",-0.41,-0.38538461538461533]
[6,29,2018,18,21,9,-0.39,-0.39,"2018-06-29T18:21:09",-0.39999999999999997,-0.38423076923076926]
[6,29,2018,18,21,19,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:21:19",-0.40499999999999997,-0.38884615384615384]
[6,29,2018,18,21,29,-0.36,-0.36,"2018-06-29T18:21:29",-0.39499999999999996,-0.38769230769230761]
[6,29,2018,18,21,39,-0.39,-0.39,{"$f":"DATE(C12217,A12217,B12217)+TIME(D12217,E12217,F12217)","v":"2018-06-29T18:21:39"},-0.39500000000000002,-0.38884615384615384]
[6,29,2018,18,21,49,-0.48,-0.48,"2018-06-29T18:21:49",-0.41500000000000004,-0.3946153846153847]
[6,29,2018,18,21,59,-0.39,-0.39,"2018-06-29T18:21:59",-0.41,-0.39692307692307693]
[6,29,2018,18,22,9,-0.33,-0.33,"2018-06-29T18:22:09",-0.39999999999999997,-0.39692307692307693]
[6,29,2018,18,22,19,-0.39,-0.39,"2018-06-29T18:22:19",{"$f":"AVERAGE(G12216:G12221)","v":-0.39000000000000007},-0.39692307692307699]
[6,29,2018,18,22,29,-0.42000000000000004,-0.42000000000000004,"2018-06-29T18:22:29",-0.39999999999999997,-0.39692307692307699]
[6,29,2018,18,22,39,-0.42000000000000004,-0.42000000000000004,"2018-06-29T18:22:39",-0.40499999999999997,-0.3946153846153847]
[6,29,2018,18,22,49,-0.36,-0.36,"2018-06-29T18:22:49",-0.38499999999999995,-0.39346153846153847]
[6,29,2018,18,22,59,-0.36,-0.36,"2018-06-29T18:22:59",-0.37999999999999995,-0.39576923076923082]
[6,29,2018,18,23,9,-0.48,-0.48,"2018-06-29T18:23:09",-0.40499999999999997,-0.39923076923076917]
[6,29,2018,18,23,19,-0.48,-0.48,"2018-06-29T18:23:19",-0.42,-0.40269230769230763]
[6,29,2018,18,23,29,-0.39,-0.39,"2018-06-29T18:23:29",-0.41500000000000004,-0.40384615384615385]
[6,29,2018,18,23,39,-0.39,-0.39,"2018-06-29T18:23:39",-0.41,-0.40384615384615385]
[6,29,2018,18,23,49,-0.39,-0.39,"2018-06-29T18:23:49",-0.41500000000000004,-0.40730769230769232]
[6,29,2018,18,23,59,-0.39,-0.39,"2018-06-29T18:23:59",-0.4200000000000001,-0.40615384615384625]
[6,29,2018,18,24,9,-0.39,-0.39,"2018-06-29T18:24:09",-0.40500000000000003,-0.40615384615384631]
[6,29,2018,18,24,19,-0.33,-0.33,"2018-06-29T18:24:19",-0.38000000000000006,-0.40153846153846168]
[6,29,2018,18,24,29,-0.36,-0.36,"2018-06-29T18:24:29",-0.375,-0.39807692307692322]
[6,29,2018,18,24,39,-0.27,-0.27,"2018-06-29T18:24:39",-0.35499999999999998,-0.39230769230769236]
[6,29,2018,18,24,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T18:24:49",-0.34,-0.38769230769230778]
[6,29,2018,18,24,59,-0.33,-0.33,"2018-06-29T18:24:59",-0.33,-0.38538461538461544]
[6,29,2018,18,25,9,-0.33,-0.33,"2018-06-29T18:25:09",-0.32,-0.38423076923076926]
[6,29,2018,18,25,19,-0.33,-0.33,"2018-06-29T18:25:19",-0.32,-0.3807692307692308]
[6,29,2018,18,25,29,-0.30000000000000004,-0.30000000000000004,"2018-06-29T18:25:29",-0.31000000000000005,-0.37730769230769234]
[6,29,2018,18,25,39,-0.33,-0.33,"2018-06-29T18:25:39",-0.32000000000000006,{"$f":"AVERAGE(G12216:G12241)","v":-0.37269230769230766}]
[6,29,2018,18,25,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T18:25:49",-0.32,-0.37038461538461537]
[6,29,2018,18,25,59,-0.27,-0.27,"2018-06-29T18:25:59",-0.31,-0.36576923076923068]
[6,29,2018,18,26,9,-0.21000000000000002,-0.21000000000000002,"2018-06-29T18:26:09",-0.29000000000000004,-0.35538461538461541]
[6,29,2018,18,26,19,-0.18,-0.18,"2018-06-29T18:26:19",-0.26500000000000001,-0.34730769230769226]
[6,29,2018,18,26,29,-0.15000000000000002,-0.15000000000000002,"2018-06-29T18:26:29",-0.24,-0.34038461538461545]
[6,29,2018,18,26,39,-0.24,-0.24,"2018-06-29T18:26:39",-0.22499999999999998,-0.33461538461538465]
[6,29,2018,18,26,49,-0.24,-0.24,"2018-06-29T18:26:49",-0.215,-0.32769230769230773]
[6,29,2018,18,26,59,-0.21000000000000002,-0.21000000000000002,"2018-06-29T18:26:59",-0.20499999999999999,-0.31961538461538463]
[6,29,2018,18,27,9,-0.21000000000000002,-0.21000000000000002,"2018-06-29T18:27:09",-0.20499999999999999,-0.31384615384615394]
[6,29,2018,18,27,19,-0.27,-0.27,"2018-06-29T18:27:19",-0.22,-0.31038461538461548]
[6,29,2018,18,27,29,-0.39,-0.39,"2018-06-29T18:27:29",-0.26,-0.30692307692307697]
[6,29,2018,18,27,39,-0.36,-0.36,"2018-06-29T18:27:39",-0.28000000000000003,-0.30230769230769233]
[6,29,2018,18,27,49,-0.51,-0.51,"2018-06-29T18:27:49",-0.32500000000000001,-0.30692307692307697]
[6,29,2018,18,27,59,-0.36,-0.36,"2018-06-29T18:27:59",-0.35000000000000003,-0.30576923076923079]
[6,29,2018,18,28,9,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:28:09",-0.38999999999999996,-0.30807692307692314]
[6,29,2018,18,28,19,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:28:19",-0.4200000000000001,-0.31038461538461537]
[6,29,2018,18,28,29,-0.39,-0.39,"2018-06-29T18:28:29",-0.42,-0.31038461538461537]
[6,29,2018,18,28,39,-0.42000000000000004,-0.42000000000000004,"2018-06-29T18:28:39",-0.42999999999999994,-0.31384615384615383]
[6,29,2018,18,28,49,-0.30000000000000004,-0.30000000000000004,"2018-06-29T18:28:49",-0.39500000000000002,-0.3115384615384616]
[6,29,2018,18,28,59,-0.27,-0.27,"2018-06-29T18:28:59",-0.37999999999999995,-0.3115384615384616]
[6,29,2018,18,29,9,-0.33,-0.33,"2018-06-29T18:29:09",-0.36000000000000004,-0.31269230769230771]
[6,29,2018,18,29,19,-0.33,-0.33,"2018-06-29T18:29:19",-0.34,-0.31269230769230771]
[6,29,2018,18,29,29,-0.48,-0.48,"2018-06-29T18:29:29",-0.35499999999999998,-0.31846153846153852]
[6,29,2018,18,29,39,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:29:39",-0.36000000000000004,-0.32307692307692309]
[6,29,2018,18,29,49,-0.51,-0.51,"2018-06-29T18:29:49",-0.39500000000000002,-0.33115384615384613]
[6,29,2018,18,29,59,-0.39,-0.39,"2018-06-29T18:29:59",-0.41500000000000004,-0.33346153846153853]
[6,29,2018,18,30,9,-0.48,-0.48,"2018-06-29T18:30:09",-0.44,-0.3403846153846154]
[6,29,2018,18,30,19,-0.48,-0.48,"2018-06-29T18:30:19",-0.46500000000000002,-0.34846153846153849]
[6,29,2018,18,30,29,-0.39,-0.39,"2018-06-29T18:30:29",-0.45,-0.35538461538461541]
[6,29,2018,18,30,39,-0.54,-0.54,"2018-06-29T18:30:39",-0.46500000000000002,-0.36923076923076931]
[6,29,2018,18,30,49,-0.54,-0.54,"2018-06-29T18:30:49",-0.47000000000000003,-0.38423076923076915]
[6,29,2018,18,30,59,-0.54,-0.54,"2018-06-29T18:30:59",-0.49500000000000005,-0.39576923076923076]
[6,29,2018,18,31,9,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:31:09",-0.51000000000000012,-0.40846153846153849]
[6,29,2018,18,31,19,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:31:19",-0.52500000000000002,-0.42230769230769233]
[6,29,2018,18,31,29,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:31:29",-0.56000000000000016,-0.43730769230769229]
[6,29,2018,18,31,39,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:31:39",-0.56500000000000006,-0.44884615384615384]
[6,29,2018,18,31,49,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:31:49",-0.57500000000000007,-0.45692307692307688]
[6,29,2018,18,31,59,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:31:59",-0.58500000000000008,-0.46615384615384614]
[6,29,2018,18,32,9,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:32:09",-0.58500000000000008,-0.46846153846153843]
[6,29,2018,18,32,19,-0.57000000000000006,-0.57000000000000006,{"$f":"DATE(C12281,A12281,B12281)+TIME(D12281,E12281,F12281)","v":"2018-06-29T18:32:19"},-0.58500000000000008,-0.47653846153846158]
[6,29,2018,18,32,29,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:32:29",-0.56000000000000005,-0.47653846153846147]
[6,29,2018,18,32,39,-0.51,-0.51,"2018-06-29T18:32:39",-0.54999999999999993,-0.47884615384615381]
[6,29,2018,18,32,49,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:32:49",-0.54500000000000004,-0.48576923076923073]
[6,29,2018,18,32,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:32:59",{"$f":"AVERAGE(G12280:G12285)","v":-0.52},-0.48692307692307685]
[6,29,2018,18,33,9,-0.54,-0.54,"2018-06-29T18:33:09",-0.51500000000000001,-0.49615384615384611]
[6,29,2018,18,33,19,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:33:19",-0.51500000000000001,-0.50769230769230766]
[6,29,2018,18,33,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:33:29",-0.53500000000000014,-0.51692307692307693]
[6,29,2018,18,33,39,-0.63,-0.63,"2018-06-29T18:33:39",-0.55500000000000005,-0.52846153846153843]
[6,29,2018,18,33,49,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:33:49",-0.55999999999999994,-0.533076923076923]
[6,29,2018,18,33,59,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:33:59",-0.58500000000000008,-0.53884615384615386]
[6,29,2018,18,34,9,-0.54,-0.54,"2018-06-29T18:34:09",-0.58500000000000008,-0.54000000000000015]
[6,29,2018,18,34,19,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:34:19",-0.58500000000000008,-0.54692307692307707]
[6,29,2018,18,34,29,-0.51,-0.51,"2018-06-29T18:34:29",-0.57500000000000007,-0.54807692307692313]
[6,29,2018,18,34,39,-0.69000000000000006,-0.69000000000000006,"2018-06-29T18:34:39",-0.58500000000000008,-0.55615384615384622]
[6,29,2018,18,34,49,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:34:49",-0.58500000000000008,-0.56423076923076931]
[6,29,2018,18,34,59,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:34:59",-0.58500000000000008,-0.56653846153846155]
[6,29,2018,18,35,9,-0.75,-0.75,"2018-06-29T18:35:09",-0.62,-0.57461538461538464]
[6,29,2018,18,35,19,-0.84000000000000008,-0.84000000000000008,"2018-06-29T18:35:19",-0.66500000000000004,-0.58615384615384625]
[6,29,2018,18,35,29,-0.66,-0.66,"2018-06-29T18:35:29",-0.69000000000000006,-0.58961538461538465]
[6,29,2018,18,35,39,-0.69000000000000006,-0.69000000000000006,"2018-06-29T18:35:39",-0.69000000000000006,-0.59423076923076923]
[6,29,2018,18,35,49,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:35:49",-0.69000000000000006,-0.59423076923076923]
[6,29,2018,18,35,59,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:35:59",-0.69000000000000006,-0.59538461538461529]
[6,29,2018,18,36,9,-0.66,-0.66,"2018-06-29T18:36:09",-0.67499999999999993,-0.59769230769230763]
[6,29,2018,18,36,19,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:36:19",-0.63500000000000012,{"$f":"AVERAGE(G12280:G12305)","v":-0.59769230769230763}]
[6,29,2018,18,36,29,-0.54,-0.54,"2018-06-29T18:36:29",-0.6150000000000001,-0.59653846153846146]
[6,29,2018,18,36,39,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:36:39",-0.57500000000000007,-0.59192307692307677]
[6,29,2018,18,36,49,-0.48,-0.48,"2018-06-29T18:36:49",-0.55500000000000005,-0.59307692307692306]
[6,29,2018,18,36,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:36:59",-0.52999999999999992,-0.59076923076923071]
[6,29,2018,18,37,9,-0.54,-0.54,"2018-06-29T18:37:09",-0.51000000000000012,-0.58961538461538454]
[6,29,2018,18,37,19,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:37:19",-0.48500000000000004,-0.58961538461538454]
[6,29,2018,18,37,29,-0.54,-0.54,"2018-06-29T18:37:29",-0.48500000000000004,-0.58961538461538443]
[6,29,2018,18,37,39,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:37:39",-0.51,-0.59076923076923049]
[6,29,2018,18,37,49,-0.48,-0.48,"2018-06-29T18:37:49",-0.51,-0.58730769230769209]
[6,29,2018,18,37,59,-0.48,-0.48,"2018-06-29T18:37:59",-0.51500000000000001,-0.58153846153846156]
[6,29,2018,18,38,9,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:38:09",-0.52500000000000002,-0.58153846153846145]
[6,29,2018,18,38,19,-0.54,-0.54,"2018-06-29T18:38:19",-0.54,-0.57923076923076899]
[6,29,2018,18,38,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:38:29",-0.54500000000000004,-0.58038461538461528]
[6,29,2018,18,38,39,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:38:39",-0.54,-0.58038461538461528]
[6,29,2018,18,38,49,-0.48,-0.48,"2018-06-29T18:38:49",-0.54000000000000015,-0.57923076923076922]
[6,29,2018,18,38,59,-0.48,-0.48,"2018-06-29T18:38:59",-0.54,-0.57115384615384612]
[6,29,2018,18,39,9,-0.48,-0.48,"2018-06-29T18:39:09",-0.52,-0.56653846153846155]
[6,29,2018,18,39,19,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:39:19",-0.505,-0.5607692307692308]
[6,29,2018,18,39,29,-0.54,-0.54,"2018-06-29T18:39:29",-0.5,-0.5526923076923077]
[6,29,2018,18,39,39,-0.51,-0.51,"2018-06-29T18:39:39",-0.48999999999999994,-0.54]
[6,29,2018,18,39,49,-0.54,-0.54,"2018-06-29T18:39:49",-0.5,-0.53538461538461546]
[6,29,2018,18,39,59,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:39:59",-0.51500000000000001,-0.53076923076923077]
[6,29,2018,18,40,9,-0.54,-0.54,"2018-06-29T18:40:09",-0.52500000000000002,-0.52846153846153854]
[6,29,2018,18,40,19,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:40:19",-0.54500000000000004,-0.52730769230769237]
[6,29,2018,18,40,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:40:29",-0.55000000000000016,-0.52384615384615385]
[6,29,2018,18,40,39,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:40:39",-0.56000000000000005,-0.52269230769230779]
[6,29,2018,18,40,49,-0.63,-0.63,"2018-06-29T18:40:49",-0.57500000000000007,-0.52615384615384619]
[6,29,2018,18,40,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:40:59",-0.55500000000000005,-0.52615384615384619]
[6,29,2018,18,41,9,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:41:09",-0.54,-0.52500000000000002]
[6,29,2018,18,41,19,-0.54,-0.54,"2018-06-29T18:41:19",-0.53500000000000003,-0.52846153846153854]
[6,29,2018,18,41,29,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:41:29",-0.53500000000000003,-0.52961538461538471]
[6,29,2018,18,41,39,-0.63,-0.63,"2018-06-29T18:41:39",-0.54500000000000004,-0.53653846153846174]
[6,29,2018,18,41,49,-0.63,-0.63,"2018-06-29T18:41:49",-0.54499999999999993,-0.54000000000000015]
[6,29,2018,18,41,59,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:41:59",-0.56499999999999995,-0.53884615384615386]
[6,29,2018,18,42,9,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:42:09",-0.56500000000000006,-0.5376923076923078]
[6,29,2018,18,42,19,-0.51,-0.51,"2018-06-29T18:42:19",-0.56000000000000005,-0.53884615384615386]
[6,29,2018,18,42,29,-0.48,-0.48,"2018-06-29T18:42:29",-0.54500000000000004,-0.53423076923076929]
[6,29,2018,18,42,39,-0.51,-0.51,"2018-06-29T18:42:39",-0.52500000000000002,-0.53307692307692323]
[6,29,2018,18,42,49,-0.54,-0.54,"2018-06-29T18:42:49",-0.5099999999999999,-0.53192307692307694]
[6,29,2018,18,42,59,-0.54,-0.54,{"$f":"DATE(C12345,A12345,B12345)+TIME(D12345,E12345,F12345)","v":"2018-06-29T18:42:59"},-0.505,-0.53076923076923077]
[6,29,2018,18,43,9,-0.51,-0.51,"2018-06-29T18:43:09",-0.51500000000000001,-0.53192307692307694]
[6,29,2018,18,43,19,-0.54,-0.54,"2018-06-29T18:43:19",-0.52,-0.53423076923076929]
[6,29,2018,18,43,29,-0.54,-0.54,"2018-06-29T18:43:29",-0.53,-0.53653846153846163]
[6,29,2018,18,43,39,-0.54,-0.54,"2018-06-29T18:43:39",{"$f":"AVERAGE(G12344:G12349)","v":-0.53500000000000003},-0.53999999999999992]
[6,29,2018,18,43,49,-0.51,-0.51,"2018-06-29T18:43:49",-0.52999999999999992,-0.53884615384615386]
[6,29,2018,18,43,59,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:43:59",-0.53500000000000003,-0.5411538461538461]
[6,29,2018,18,44,9,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:44:09",-0.54500000000000004,-0.54230769230769227]
[6,29,2018,18,44,19,-0.54,-0.54,"2018-06-29T18:44:19",-0.54500000000000004,-0.54115384615384621]
[6,29,2018,18,44,29,-0.54,-0.54,"2018-06-29T18:44:29",-0.54500000000000004,-0.54115384615384621]
[6,29,2018,18,44,39,-0.63,-0.63,"2018-06-29T18:44:39",-0.56000000000000005,-0.54346153846153844]
[6,29,2018,18,44,49,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:44:49",-0.57500000000000007,-0.54461538461538461]
[6,29,2018,18,44,59,-0.54,-0.54,"2018-06-29T18:44:59",-0.57000000000000006,-0.54346153846153844]
[6,29,2018,18,45,9,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:45:09",-0.57500000000000007,-0.54230769230769227]
[6,29,2018,18,45,19,-0.63,-0.63,"2018-06-29T18:45:19",-0.59,-0.5492307692307693]
[6,29,2018,18,45,29,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:45:29",-0.6,-0.55500000000000005]
[6,29,2018,18,45,39,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:45:39",-0.59500000000000008,-0.55730769230769228]
[6,29,2018,18,45,49,-0.51,-0.51,"2018-06-29T18:45:49",-0.58000000000000007,-0.55499999999999994]
[6,29,2018,18,45,59,-0.54,-0.54,"2018-06-29T18:45:59",-0.58000000000000007,-0.55153846153846153]
[6,29,2018,18,46,9,-0.57000000000000006,-0.57000000000000006,"2018-06-29T18:46:09",-0.57500000000000007,-0.5492307692307693]
[6,29,2018,18,46,19,-0.60000000000000009,-0.60000000000000009,"2018-06-29T18:46:19",-0.57000000000000006,-0.55038461538461536]
[6,29,2018,18,46,29,-0.51,-0.51,"2018-06-29T18:46:29",-0.55500000000000005,-0.5526923076923077]
[6,29,2018,18,46,39,-0.51,-0.51,"2018-06-29T18:46:39",-0.54,-0.5526923076923077]
[6,29,2018,18,46,49,-0.39,-0.39,"2018-06-29T18:46:49",-0.52000000000000013,-0.5492307692307693]
[6,29,2018,18,46,59,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:46:59",-0.505,{"$f":"AVERAGE(G12344:G12369)","v":-0.54692307692307696}]
[6,29,2018,18,47,9,-0.51,-0.51,"2018-06-29T18:47:09",-0.49499999999999994,-0.54576923076923078]
[6,29,2018,18,47,19,-0.51,-0.51,"2018-06-29T18:47:19",-0.48,-0.5446153846153845]
[6,29,2018,18,47,29,-0.51,-0.51,"2018-06-29T18:47:29",-0.48,-0.54461538461538461]
[6,29,2018,18,47,39,-0.51,-0.51,"2018-06-29T18:47:39",-0.48,-0.54346153846153844]
[6,29,2018,18,47,49,-0.44999999999999996,-0.44999999999999996,"2018-06-29T18:47:49",-0.49000000000000005,-0.53999999999999992]
[6,29,2018,18,47,59,-0.42000000000000004,-0.42000000000000004,"2018-06-29T18:47:59",-0.48500000000000004,-0.53538461538461524]
[6,29,2018,18,48,9,-0.42000000000000004,-0.42000000000000004,"2018-06-29T18:48:09",-0.47,-0.53192307692307683]
[6,29,2018,18,48,19,-0.48,-0.48,"2018-06-29T18:48:19",-0.46500000000000002,-0.52846153846153843]
[6,29,2018,18,48,29,-0.39,-0.39,"2018-06-29T18:48:29",-0.44500000000000001,-0.52153846153846151]
[6,29,2018,18,48,39,-0.36,-0.36,"2018-06-29T18:48:39",-0.42,-0.51461538461538459]
[6,29,2018,18,48,49,-0.39,-0.39,"2018-06-29T18:48:49",-0.41,-0.50884615384615384]
[6,29,2018,18,48,59,-0.39,-0.39,"2018-06-29T18:48:59",-0.40500000000000003,-0.49961538461538463]
[6,29,2018,18,49,9,-0.33,-0.33,"2018-06-29T18:49:09",-0.39000000000000007,-0.48923076923076925]
[6,29,2018,18,49,19,-0.33,-0.33,"2018-06-29T18:49:19",-0.36500000000000005,-0.48115384615384615]
[6,29,2018,18,49,29,-0.24,-0.24,"2018-06-29T18:49:29",-0.34,-0.46730769230769231]
[6,29,2018,18,49,39,-0.24,-0.24,"2018-06-29T18:49:39",-0.32,-0.45230769230769236]

{"sheet":"Tab 6 Tracer Tests","index":5,"n_rows":10,"n_cols":10,"rows_kept":10,"cut":false,"hidden":false,"merged":[[0,0,0,14],[5,0,5,16],[6,0,6,16],[2,0,2,16],[4,0,4,16],[3,0,3,16]]}
["Description of Field Methods"]
[]
["This Tab provides suggested operating procedures for data collection for use with this spreadsheet model.  These methods are described in more detail in the Final Report for ESTCP ER201322, available online at: https://www.serdp-estcp.org/Program-Areas/Environmental-Restoration/Contaminated-Groundwater/Emerging-Issues/ER-201322/ER-201322"]
["Figure 6.1: Typical Apparatus for Pneumatic and Tracer Testing"]
["Flow and Vacuum Testing: Refer to the schematic diagram above for details of a suggested apparatus. The general goal is to extract gas at a measured flow rate and measure static vacuum at two or more radial distances, with at least one monitoring point near the extraction point (suggested radius of about 3 ft or 1 m), and at least one near the far end of the region of induced vacuum clearly higher than baseline cross-slab pressure fluctuations (i.e., near the extent but within the radius of influence).  Additional monitoring points are valuable and encouraged, to the extent that time, budget, access and practical constraints allow.  Consider specifically monitoring points near possible preferential pathways below or across the floor, in different compass directions to assess anisotropy, and possibly on both sides of suspected barriers to flow (footers, etc.). The monitoring points that are near possible preferential pathways should be in addition to the near and far monitoring points mentioned above, as they will not typically be representative of the majority of the building.  Measure the flow rate using a thermal anemometer, vane anemometer, pitot tube, or critical orifice flowmeter (more than one method can be helpful for assessing the uncertainty in the flow measurement).  Measure applied vacuum at the top of the suction pit to compare to gas extraction flow rate and consider testing at a few different flow rates to help with fan selection.  Visually observe transient response in vacuum measurements after turning on the fan to verify stable readings before recording vacuum vs distance data.  Consider using a micromanometer with a datalogger to record transient drawdown and recovery cycles in response to turning the fan on and off once or twice.  The transient data can be analysed using AQTESOLV(R) software to provide an independent line of evidence to support T and B values derived from fitting this spreadsheet model to the static vacuum vs distance data.  The ideal design of a suction pit involves coring a 4 to 6-inch diameter (10 to 15 cm) hole in the floor, removing 3 to 10 gallons (10 to 40 L) of soil to minimize resistance to flow and setting a PVC pipe using an air-tight gasket or backer-rod and fast-setting achor cement  to form a seal between the pipe and the concrete.  The extracted gas should be discharged to an outdoor location to avoid adverse effects on indoor air quality, but may be filtered using activated carbon or other appropriate filters where there are no nearby doors or windows to discharge through.  It may be valuable to monitor the extracted gas using a photoionization meter for volatile organic compounds and/or a continuous radon meter  for a period of time during the  diagnostic testing to assist in understanding the subsurface distribution of chemicals of concern and it may also be helpful to use a landfill gas meter to monitor oxygen and carbon dioxide to assist in assessing the degree to which indoor air is drawn across the floor slab during the diagnostic testing.  These field-screening measurements should be made at the same ambient pressure the instruments were calibrated at, so using a vacuum chamber to fill a Tedlar bag is recommended over direct monitoring of the influent or effluent of the fan, which would be under negative or positive pressure, respectively."]
["Interwell tracer test: The Interwell Test involves injecting a fixed volume (e.g. 5 to 10 L) of 100% helium into a subslab probe or monitoring point, at a certain distance (typically 5 to 15 ft) from the suction point and monitoring the concentration of helium in the extracted gas with a portable meter.    The average travel time is the time interval between the midpoint of injection and the highest concentration of helium in the gas extracted from the suction point.  Typical data is shown in Figure 6.2, below.  The operator only needs to record the time associated with the peak reading, recorded with a stopwatch that begins at the time helium is injected.  Optimal test durations are in the range of about 1 to 3 minutes, and a corresponding radial distance for the helium interwell test can be selected from Figure 2.2 on Tab 2 after the vacuum vs distance data has been used to select appropriate T and B values to fit the curves on Figure 2.1a and Figure 2.1b of Tab 2 (step 4 on the Home Page Tab)."]
["Helium Flood tracer test: The Flood Test involves reversing the flow direction on the fan, blower or vacuum to blow air into the subsurface (ideally at the same flow rate as would be used for extraction to mimic the conditions), but adding about 1%v/v helium to the injected air.  Helium concentrations are monitored at all one or more subslab probes or monitoring points, at measured distance(s) from the point of injection.  The average travel time is the time interval between the start of helium injection and the arrival of a helium concentration equal to 50% of the concentration injected.  A typical plot is shown in Figure 6.3, below."]
[]
[]
[null,"Figure 6.2: Typical data for a Helium Inter-Well Tracer Test",null,null,null,null,null,null,null,"Figure 6.3: Typical data for a Helium Flood Tracer Test"]

{"sheet":"Tab 7 H-J Model Assumptions","index":6,"n_rows":13,"n_cols":2,"rows_kept":13,"cut":false,"hidden":false,"merged":[[0,0,0,1],[1,0,1,1],[2,0,2,1]]}
["MODEL ASSUMPTIONS"]
[]
[]
["Hantush-Jacob (1955) Model Assumptions","Application to Subslab Gas Extraction"]
["The aquifer (in this application, the subfloor materials) and aquitard (floor slab) have infinite areal extent","This assumption is reasonable if the building is large relative to the radius of influence (ROI) of the gas extraction, which depends on the relative permeability of the floor and subfloor materials and extraction flow rate, but is typically in the range of 10 to 30 m.  The suction point should ideally be located far enough from subslab obstructions or discontinuities that the radial flow pattern is not significantly biased by barriers (e.g., footers) or sources of leakage (e.g., perimeter expansion joints at exterior walls).   "]
["The aquifer (subfloor) is homogeneous, isotropic and of uniform thickness","Building Codes typically specify a layer of 10 to 15 cm of compacted granular fill below a concrete floor slab as a capillary break, which can be visually verified during installation of suction points and sub-slab probes.  Where present, construction aggregate tends to be very homogenous, isotropic and uniform thickness by design.  This layer may be disrupted by utilities or footers, and may be absent in buildings constructed prior to promulgation of building codes."]
["The aquitard (floor slab) is homogeneous, isotropic and of uniform thickness","Slab thickness is usually uniform by design, but the slab is neither uniform, nor homogenous, so it is appropriate to explicitly consider the uncertainty that this assumption imposes.  A concrete floor slab is generally a dual porosity medium, analogous to fractured rock.  Mathematical modeling of fluid flow through fractured rock often adopts a simplifying assumption that the fractured rock behaves as an equivalent porous medium, as long as the hydraulic properties are measured at a scale at least the size of a representative elemental volume (REV), as described by Bear, 1979.  An REV is the smallest volume within which a measurement can be made that will yield a value representative of the whole system of interest.  In attempts to measure Qsoil, the REV would be no larger than the area of the building.  Irregular spacing of discontinuities in the concrete (floor drains, expansion joints, fractures, etc.) are to be expected and are likely to cause spatial variability in the gas conductivity of the floor, so it is prudent to explicitly consider the range of bulk gas conductivity values observed for a particular floor slab.   Comparisons between the measured vacuum and the mathematical model provides insight into the degree to which the floor slab approximates an equivalent porous medium at the large scale.  To account for spatial variability, it is advisable to have multiple monitoring points, and the range of fitted T and B values should be assessed using a sensitivity analysis.  Locations with relatively low vacuum are indications of nearby air supply (e.g. leakage across the floor or subsurface utilities), which should be compared to visual observations of expansion joints, floor drains and other features to aid in interpretation."]
["Extraction well is fully penetrating the active flow zone","This is simple to achieve if there is a granular fill layer below the floor slab and the gravel is removed prior to installation of the suction point.  If there is no granular fill layer, the thickness of the active flow zone is a variable (b) that can be quantified by adding subslab helium tracer testing.  Corrections for partially-penetrating well screens are available in AQTESOLV, see the ESTCP ER201322 final report for a description of transient pneumatic testing and curve-fitting using AQTESOLV."]
["Flow to pumping well is horizontal and radial when pumping well is fully penetrating","Where a granular fill layer exists below the floor slab, it is usually the material with the highest gas permeability and this assumption is appropriate.   If a granular fill layer is not present, flow may still be radial toward a suction point, as long as the suction point is not adjacent to a footer or exterior wall.  Flow may also follow a hemispherical pattern, depending on the vertical profile of gas conductivity below the slab and thickness of the unsaturated zone above the water table and capillary fringe.  If the region of flow extends vertically, a larger \"b\" value will be needed to match the tracer test data to the model curves in Figure 2.2, compared to a typical 4 to 6 inch (10 to 15 cm) grular fill layer. "]
["Aquifer is leaky confined","This is appropriate where downward flow of indoor air across the floor is the dominant supply of air to the subslab venting system.  Some of the extracted gas may also originate from outdoor air that flows into the subsurface beside the building and through the soil beneath the granular fill or from preferential pathways such as subsurface utilities.  This process will tend to result in an overestimation of the floor slab leakance (B), which will bias the analysis toward a smaller ROI, which is protective."]
["Water is released instantaneously from storage and the diameter of pumping well is very small so that storage in the well can be neglected with decline of hydraulic head","Very early-time transient data (the first few seconds after the start of extraction) primarily affects the storage parameter (S), which is not used in subsequent calculations.  Vent-pipes are typically 5 to 15 cm (2 to 5 inches) in diameter and the length of pipe between the suction point and fan during diagnostic testing is often less than a few m (10 ft), so the dead volume is usually flushed within seconds at typical flow rates of 5 to 50 L/s (10 to 100 standard cubic feet per minute).  In most cases, the steady vacuum distribution is achieved within minutes, and this can easily be confirmed using a pressure transducer with data logging capabilities.  It is advisable to use a valve to initiate and cease flow in the transient analysis because a valve can usually be opened and closed faster than the time needed for a fan to achieve steady flow after being powered or to stop after power is cut. "]
["Aquitard is overlain by an infinite constant-head plane source","Indoor air is an infinite source of air much greater than needed to meet the demands of a subslab suction point.  Indoor air pressures are not usually affected by subslab gas extraction to any significant degree."]
["Flow is vertical in the aquitard","Air flow across concrete is usually through discontinuities such as expansion joints, utility penetrations, etc.  The model approximates this as vertical flow through a porous medium.  The distinction is evident in the variability in the vacuum vs distance data relative to the model of vacuum vs distance (Figure 2.1a and Figure 2.1b on Tab 2)"]

{"sheet":"Calculations","index":7,"n_rows":490,"n_cols":25,"rows_kept":490,"cut":false,"hidden":false,"merged":[[397,0,397,1],[397,7,397,9],[397,12,397,13],[395,12,395,13],[203,0,203,1],[203,12,203,13],[201,12,201,13],[7,7,7,9],[300,0,300,1],[300,12,300,13],[300,7,300,9],[203,7,203,9],[7,0,7,1],[7,12,7,13],[298,12,298,13],[5,12,5,13],[103,12,103,13],[105,0,105,1],[105,12,105,13],[105,7,105,9]]}
["Calculations based on the Hantush-Jacob Leaky Aquifer Model (1955)"]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Qw (scfm)","Qw (L/min)"]
["Test ID",null,null,null,null,null,null,null,null,null,null,null,"Effective Porosity, n = ",null,{"$f":"'Tab 2   Inputs and Plots'!R36","v":0.25},null,null,null,null,{"$f":"'Tab 2   Inputs and Plots'!$N$36","v":15},{"$f":"T6*28.3","v":424.5}]
[{"$f":"'Tab 2   Inputs and Plots'!M36","v":"Upper bound"}]
["Radius, r",null,"Transmissivity, T","Thickness, b","Conductivity, K","Leakance, B","r/B","Flow Rate, Qw",null,null,"Ko(r/B)","K1(r/B)","Vacuum",null,"Velocity","Travel Time","Cummulative Travel Time","Time for 500 Pore Volumes","Q(r)/Qw","Qr","Qr","Qleak","Delta Q","Delta A","Qleak/A"]
["(ft)","(m)","(ft2/d)","(ft)","(ft/d)","B (ft)","(dim)","(ft3/min)","(ft3/day)","(L/min)","(dim)","(dim)","(ft-air)","(Pa)","(ft/day)","(min)","(min)","(days)","(%)","(scfm)","(L/min)","(L/min)","(L/min)","(ft2)","(L/min per 1000 ft2)"]
[0.1,{"$f":"A10*0.3048","v":3.0480000000000004E-2},{"$f":"'Tab 2   Inputs and Plots'!O36","v":98},{"$f":"'Tab 2   Inputs and Plots'!Q36","v":0.5},{"$f":"C10/D10","v":196},{"$f":"'Tab 2   Inputs and Plots'!P36","v":16},{"$f":"(A10/F10)","v":6.2500000000000003E-3},{"$f":"'Tab 2   Inputs and Plots'!$N$36","v":15},{"$f":"(H10*1440)","v":21600},{"$f":"H10*28.3","v":424.5},{"$f":"BESSELK(G10,0)","v":5.1911657959313322},{"$f":"BESSELK(G10,1)","v":159.98221519772952},{"$f":"(I10*K10/(2*PI()*C10))","v":182.10115766910377},{"$f":"(M10*0.015)*249","v":680.14782389410254},{"$f":"(I10/(2*3.14159*O$6*D10))*(1/F10)*L10","v":274989.40411312087}]
[{"$f":"A10*1.1","v":0.11000000000000001},{"$f":"A11*0.3048","v":3.3528000000000009E-2},{"$f":"$C$10","v":98},{"$f":"$D$10","v":0.5},{"$f":"C11/D11","v":196},{"$f":"$F$10","v":16},{"$f":"(A11/F11)","v":6.8750000000000009E-3},{"$f":"$H$10","v":15},21600,{"$f":"H11*28.3","v":424.5},{"$f":"BESSELK(G11,0)","v":5.0958671865699721},{"$f":"BESSELK(G11,1)","v":145.43530978002312},{"$f":"(I11*K11/(2*PI()*C11))","v":178.75817311203937},{"$f":"(M11*0.015)*249","v":667.66177657346702},{"$f":"(I11/(2*3.14159*O$6*D11))*(1/F11)*L11","v":249985.09443056697},{"$f":"(A11-A10)/((O10+O11)/2)*1440","v":5.4859807628547729E-5},{"$f":"P11","v":5.4859807628547729E-5},{"$f":"Q11*500/1440","v":1.9048544315467961E-5},{"$f":"G11*BESSELK(G11,1)*100","v":99.986775473765903},{"$f":"H10*S11/100","v":14.998016321064886},{"$f":"T11*28.3","v":424.44386188613629},{"$f":"J11-U11","v":5.6138113863710259E-2}]
[{"$f":"A11*1.1","v":0.12100000000000002},3.6880800000000012E-2,{"$f":"$C$10","v":98},{"$f":"$D$10","v":0.5},196,{"$f":"$F$10","v":16},7.5625000000000015E-3,{"$f":"$H$10","v":15},21600,424.5,5.0005707705112012,132.2106060811256,175.41526549394328,655.17601661987817,227253.48401226077,{"$f":"(A12-A11)/((O11+O12)/2)*1440","v":6.6381892476857323E-5},{"$f":"Q11+(P12)","v":1.2124170010540506E-4},{"$f":"Q12*500/1440","v":4.2097812536598979E-5},{"$f":"G12*BESSELK(G12,1)*100","v":99.984270848851253},{"$f":"H11*S12/100","v":14.997640627327687},{"$f":"T12*28.3","v":424.43322975337355},{"$f":"J12-U12","v":6.677024662644726E-2},{"$f":"V12-V11","v":1.0632132762737001E-2},{"$f":"(3.14159*A12*A12)-(3.14159*A11*A11)","v":7.9827801900000106E-3},{"$f":"1000*W12/X12","v":1331.8834428205628}]
[0.13310000000000002,4.0568880000000009E-2,98,0.5,196,16,8.3187500000000015E-3,15,21600,424.5,4.9052769586893543,120.18788577412296,172.07244923000098,642.69059787405365,206587.93260109183,8.0324281328486384E-5,{"$f":"Q12+(P13)","v":2.0156598143389144E-4},6.9988187997878978E-5,99.981297478348552,14.997194621752282,424.4206077955896,7.9392204410396516E-2,{"$f":"V13-V12","v":1.2621957783949256E-2},{"$f":"(3.14159*A13*A13)-(3.14159*A12*A12)","v":9.6591640299000039E-3},{"$f":"1000*W13/X13","v":1306.7339725133463}]
[0.14641000000000004,4.4625768000000017E-2,98,0.5,196,16,9.1506250000000025E-3,15,21600,424.5,4.8099862379081921,109.25785827853267,168.72974139682537,630.20558411714285,187800.58336831874,9.7195527881377777E-5,2.9876150931526925E-4,1.0373663517891292E-4,99.977768940999823,14.996665341149974,424.40562915454427,9.4370845455728158E-2,1.4978641045331642E-2,1.1687588476179019E-2,1281.58525395211]
[0.16105100000000006,4.9088344800000017E-2,98,0.5,196,16,1.0065687500000003E-2,15,21600,424.5,4.7146991845845898,99.32116727187973,165.38716221457204,617.72105087142654,170720.65523131617,1.176111076841599E-4,4.1637261699942912E-4,1.4457382534702401E-4,99.973583189396919,14.996037478409537,424.38786063898993,0.11213936101006539,1.7768515554337228E-2,1.4141982056176602E-2,1256.4374274945931]
[0.17715610000000007,5.3997179280000022E-2,98,0.5,196,16,1.1072256250000004E-2,15,21600,424.5,4.6194164809190292,90.287487518891453,162.04473561418493,605.23708751898062,155192.89041600397,1.4231592586271943E-4,5.5868854286214857E-4,1.9398907738269047E-4,99.968619797784328,14.995292969667648,424.36679104159447,0.13320895840553248,2.1069597395467099E-2,1.7111798287973698E-2,1231.2906592800928]
[0.19487171000000009,5.9396897208000031E-2,98,0.5,196,16,1.2179481875000005E-2,15,21600,424.5,4.5241389339062055,82.074703808271124,158.70248990427015,592.75379979244894,141076.14315192756,1.7221157468116379E-4,7.3090011754331236E-4,2.5378476303587234E-4,99.962736742883209,14.994410511432482,424.34181747353927,0.15818252646073461,2.4973568055202122E-2,2.0705275928448161E-2,1206.1451458799208]
[0.21435888100000011,6.5336586928800039E-2,98,0.5,196,16,1.3397430062500007E-2,15,21600,424.5,4.4288674976656983,74.608164533499078,155.36045855443501,580.27131270081475,128242.09667107899,2.0838934829250189E-4,9.392894658358142E-4,3.261421756374355E-4,99.955766642904734,14.993364996435709,424.31222939913056,0.18777060086944175,2.9588074408707143E-2,2.5053383873422291E-2,1181.001119776696]
[0.23579476910000013,7.187024562168004E-2,98,0.5,196,16,1.4737173068750008E-2,15,21600,424.5,4.3336032996489884,67.82000313275249,152.01868111460479,567.7897739630489,116574.09684804939,2.521702377631995E-4,1.1914597035990137E-3,4.1370128597187968E-4,99.94751236905411,14.992126855358118,424.27719000663473,0.22280999336527429,3.5039392495832544E-2,3.0314594486840984E-2,1155.8588557416629]
[0.25937424601000014,7.9057270183848047E-2,98,0.5,196,16,1.6210890375625009E-2,15,21600,424.5,4.2383476713665633,61.648521220001349,148.67720429290071,555.30935803398404,105966.09187959196,3.051533922437317E-4,1.4966130958427454E-3,5.1965732494539771E-4,99.937741931683405,14.990661289752511,424.23571449999605,0.26428550000395035,4.1475506638676052E-2,3.6680659329077575E-2,1130.7186783798484]
[0.28531167061100016,8.6962997202232856E-2,98,0.5,196,16,1.783197941318751E-2,15,21600,424.5,4.143102184378316,56.037627800235839,145.33608321814884,542.83027081978594,96321.668365787249,3.6927485261722053E-4,1.8658879484599658E-3,6.478777598819326E-4,99.926182529766962,14.988927379465045,424.18664483886079,0.31335516113921358,4.9069661135263232E-2,4.4383597788183848E-2,1105.5809709127939]
[0.31384283767210019,9.5659296922456144E-2,98,0.5,196,16,1.9615177354506262E-2,15,21600,424.5,4.0478686924036236,50.936329471710266,141.99538291706136,530.35275519522418,87553.175031508072,4.4687875523257564E-4,2.3127667036925417E-3,8.0304399433768817E-4,99.912513637516113,14.986877045627416,424.12862039125588,0.37137960874412101,5.8024447604907436E-2,5.3704153323702486E-2,1080.4461855150071]
[0.34522712143931022,0.10522522661470177,98,0.5,196,16,2.1576695089956889E-2,15,21600,424.5,3.9526493805353051,46.298266981684549,138.65518004061568,517.87709745169946,79580.926123745172,5.4080368174298169E-4,2.8535703854355235E-3,9.9082305049844554E-4,99.896358985722614,14.984453847858392,424.06004389439249,0.4399561056075072,6.8576496863386183E-2,6.4982025521680087E-2,1055.3148553442193]
[0.37974983358324127,0.11574774927617194,98,0.5,{"$f":"C24/D24","v":196},16,{"$f":"(A24/F24)","v":2.3734364598952579E-2},15,{"$f":"(H24*1440)","v":21600},424.5,3.8574468226856693,42.081293923620798,135.31556487920699,505.4036348238381,72332.477244819442,6.544874169746597E-4,3.5080578024101832E-3,1.2180756258368692E-3,99.877277277890371,14.981591591683555,423.97904204464464,0.52095795535535672,8.1001849747849519E-2,7.862825088123282E-2,1030.1876086522896]
[0.41772481694156544,0.12732252420378914,98,0.5,196,16,2.610780105884784E-2,15,21600,424.5,3.7622640485541496,38.247093746980767,131.9766437118092,492.93276426360734,65741.967040159972,7.9209409560427463E-4,4.3001518980144583E-3,1.4931082979216868E-3,99.854751462527702,14.978212719379155,423.88341995843007,0.61658004156993229,9.5622086214575575E-2,9.5140183566291725E-2,1005.0651851848496]
[0.45949729863572203,0.14005477662416807,98,0.5,196,16,2.8718581164732627E-2,15,21600,424.5,3.6671046215855174,34.760831599151153,128.63854154067488,480.4649526544207,59749.518758149934,9.5866860220720422E-4,5.2588205002216627E-3,1.8259793403547439E-3,99.828176363382511,14.974226454507377,423.7706086625588,0.72939133744119999,0.1128112958712677,0.11511962211521309,979.94845534121725]
[0.50544702849929424,0.1540602542865849,98,0.5,196,16,3.159043928120589E-2,15,21600,424.5,3.5719727295861423,31.590837835765097,125.30140527006763,468.00074868370257,54300.696243982042,1.1603241782982539E-3,6.4191446785199164E-3,2.2288696800416377E-3,99.796844449315898,14.969526667397385,423.63760468734603,0.86239531265397318,0.13300397521277318,0.13929474275940779,954.83844241343604]
[0.55599173134922375,0.16946627971524342,98,0.5,196,16,3.4749483209326484E-2,15,21600,424.5,3.4768732898834309,28.708320323664022,121.96540739515484,455.54079662090334,49346.009424458869,1.4044705354501279E-3,7.8236152139700438E-3,2.7165330604062652E-3,99.759929505512929,14.96398942582694,423.48090075090238,1.0190992490976214,0.15670393644364822,0.16854663873888365,929.73634844428773]
[0.61159090448414621,{"$f":"A29*0.3048","v":0.18641290768676777},98,0.5,196,16,3.8224431530259138E-2,15,21600,424.5,{"$f":"BESSELK(G29,0)","v":3.3818120711498576},26.08710292257231,118.6307502754791,{"$f":"(M29*0.015)*249","v":443.08585227891439},44840.464790723963,1.7000914405474637E-3,{"$f":"Q28+(P29)","v":9.5237066545175077E-3},3.3068425883741345E-3,99.716467948668836,14.957470192300326,423.29640644209923,1.2035935579007742,0.18449430880315276,0.2039414328740492,904.64358420534063]
[0.67274999493256094,0.20505419845544459,98,0.5,196,16,4.2046874683285058E-2,15,21600,424.5,{"$f":"BESSELK(G30,0)","v":3.2867958342666408},23.703387769611009,115.29767107632181,{"$f":"(M30*0.015)*249","v":430.63680147006193},40743.15679509403,2.0580828110296065E-3,{"$f":"Q29+(P30)","v":1.1581789465547113E-2},4.021454675537192E-3,99.665337511814585,14.949800626772188,423.07935773765291,1.4206422623470871,0.21704870444631297,0.24676913377759946,879.56180387587688]
[0.74002499442581704,0.22555961830098906,98,0.5,196,16,4.6251562151613565E-2,15,21600,424.5,{"$f":"BESSELK(G31,0)","v":3.1918324948702801},21.535539207216353,111.96644747068105,{"$f":"(M31*0.015)*249","v":418.19468130299367},37016.896450195061,2.491664941758712E-3,{"$f":"Q30+(P31)","v":1.4073454407305825E-2},4.8866161136478558E-3,99.605233011107785,14.940784951666167,422.82421413215252,1.6757858678474804,0.25514360550039328,0.29859065187089562,854.49294511307096]
[0.81402749386839879,0.24811558013108798,98,0.5,196,16,5.0876718366774924E-2,15,21600,424.5,{"$f":"BESSELK(G32,0)","v":3.0969313105035563},19.563887391813612,108.63740420435073,{"$f":"(M32*0.015)*249","v":405.76070470324993},33627.873756853543,3.0168857194947832E-3,{"$f":"Q31+(P32)","v":1.7090340126800607E-2},5.9341458773613225E-3,99.534638899260003,14.930195834889,422.5245421273587,1.9754578726413001,0.29967200479381972,0.36129468876378312,829.43927523315267]
[0.89543024325523879,0.27292713814419678,98,0.5,{"$f":"C33/D33","v":196},16,{"$f":"(A33/F33)","v":5.5964390203452424E-2},15,{"$f":"(H33*1440)","v":21600},424.5,{"$f":"BESSELK(G33,0)","v":3.0021030955745402},17.77054979950675,105.31092063647802,{"$f":"(M33*0.015)*249","v":393.3362885772454},30545.350894717787,3.6532357460138751E-3,{"$f":"Q32+(P33)","v":2.0743575872814481E-2},7.2026305113939175E-3,99.451798310947908,14.917769746642186,422.1728838299739,2.3271161700261018,0.3516582973848017,0.43716657340417875,804.4034443129276]
[0.98497326758076276,0.3002198519586165,98,0.5,196,16,6.1560829223797672E-2,15,21600,424.5,2.9073604676031759,16.139269007693237,101.98743937765929,380.92308607555742,27741.383389157556,4.4244014221405956E-3,2.5167977294955075E-2,8.7388810051927356E-3,99.354678317953386,14.903201747693009,421.76060945971216,2.7393905402878431,0.4122743702617413,0.52897155381905536,779.38854610463136]
[1.0834705943388392,0.33024183715447819,98,0.5,196,16,6.7716912146177449E-2,15,21600,424.5,2.8127181284919258,14.655265279365954,98.667476156646714,368.52302344507547,25190.566722129926,5.3591885518453316E-3,3.0527165846800406E-2,1.0599710363472363E-2,99.240931140174908,14.886139671026235,421.27775269004246,3.2222473099575382,0.48285676966969504,0.64005558012105812,754.39818769858869]
[1.1918176537727232,0.36326602086992604,98,0.5,196,16,7.44886033607952E-2,15,21600,424.5,2.7181931847772085,13.30510261124372,95.351631054464079,356.13834198842329,22869.806085681485,6.4926573170249972E-3,3.7019823163825405E-2,1.2854105265217155E-2,99.107851108361402,14.86617766625421,420.71282795499417,3.7871720450058319,0.56492473504829377,0.77446725194648014,729.43656898139977]
[1.3109994191499956,0.39959262295691866,98,0.5,196,16,8.1937463696874727E-2,15,21600,424.5,2.6238055109784302,12.076567028979079,92.040601250345176,343.77164567003922,20758.107186643399,7.8675200930198759E-3,4.4887343256845277E-2,1.5585883075293499E-2,98.952327251984755,14.842849087797713,420.05262918467531,4.4473708153246889,0.66019877031885699,0.93710537485523915,704.5085729241946]
[1.4420993610649953,0.43955188525261057,98,0.5,196,16,9.0131210066562203E-2,15,21600,424.5,2.5295781602312997,10.958556023605819,88.73519542635978,331.42595491745374,18836.386201723151,9.5358672483010967E-3,5.4423210505146376E-2,1.8896948092064714E-2,98.770791498980671,14.8156187248471,419.28200991317294,5.2179900868270579,0.77061927150236897,1.1338975035748424,679.61986782124052]
[1.5863092971714949,0.48350707377787167,98,0.5,196,16,9.9144331073218434E-2,15,21600,424.5,2.4355378263331886,9.9409781240841024,85.436349975525417,319.10476715858744,17087.297155279382,1.1561303774429373E-2,6.5984514279575746E-2,2.2911289680408245E-2,98.559162632581618,14.783874394887244,418.38364537530902,6.1163546246909846,0.89836453786392667,1.3720159793255577,654.77702257194994]
[1.7449402268886445,0.53185778115565885,98,0.5,196,16,0.10905876418054028,15,21600,424.5,2.3417153610925685,9.0146616921508667,82.145147149933337,306.81212460500103,15495.075149085234,1.4021602641996443E-2,8.0006116921572196E-2,2.7779901708879236E-2,98.312786365163149,14.746917954774471,417.33777812011755,7.162221879882452,1.0458672551914674,1.660139334983926,629.98763606886882]
[1.919434249577509,0.58504355927122476,98,0.5,196,16,0.11996464059859431,15,21600,424.5,2.2481463504023758,8.1712721084683597,78.862835268854241,294.55268972917054,14045.39401568287,1.701201096505587E-2,9.7018127886628058E-2,3.3686849960634743E-2,98.026372172572479,14.70395582588587,416.12194987257016,8.3780501274298445,1.2158282475473925,2.0087685953305474,605.2604816570846]
[2.1113776745352602,0.64354791519834731,98,0.5,196,16,0.13196110465845376,15,21600,424.5,2.1548717516763958,7.4032365939782752,75.590851079400167,282.33182878155964,12725.237095700804,2.0649384826914207E-2,0.11766751271354227,4.0856775247757729E-2,97.693927898926191,14.654089184838929,414.7107239309417,9.7892760690583032,1.4112259416284587,2.4306100003499669,580.60566747658652]
[2.3225154419887866,0.70790270671818223,98,0.5,196,16,0.14515721512429916,15,21600,424.5,2.061938594112104,6.7036759780276602,72.330844321078814,270.15570353922936,11522.779955802434,2.5077381336980661E-2,0.14274489405052293,4.9564199323098239E-2,97.308693606615776,14.596304040992365,413.07540436008395,11.424595639916049,1.6353195708577459,2.9410381004234623,556.03481322540028]
[2.5547669861876656,{"$f":"A44*0.3048","v":0.77869297739000054},98,0.5,{"$f":"C44/D44","v":196},16,{"$f":"(A44/F44)","v":0.1596729366367291},15,{"$f":"(H44*1440)","v":21600},424.5,{"$f":"BESSELK(G44,0)","v":1.9694007415717301},6.0663427857749204,{"$f":"(I44*K44/(2*PI()*C44))","v":69.084704486935522},{"$f":"(M44*0.015)*249","v":258.03137125870421},10427.283968686103,3.0473006802797156E-2,{"$f":"Q43+(P44)","v":0.17321790085332009},6.0145104462958364E-2,96.863076724971748,14.529461508745761,{"$f":"T44*28.3","v":411.18376069750508},13.316239302494921,{"$f":"V44-V43","v":1.891643662578872},{"$f":"(3.14159*A44*A44)-(3.14159*A43*A43)","v":3.5586561015123905},{"$f":"1000*W44/X44","v":531.56124351969379}]
[2.8102436848064323,0.85656227512900063,98,0.5,196,16,0.17564023030040202,15,21600,424.5,1.8773197155896693,5.485565072081596,65.854589693870267,245.96689250660543,9428.9997705749702,3.7054914287270799E-2,0.21027281514059087,7.3011394146038494E-2,96.348591258825294,14.452288688823794,408.99976989371339,15.500230106286608,2.1839908037916871,4.3059738828299849,507.20019749778839]
[3.0912680532870755,0.94221850264190066,98,0.5,196,16,0.19320425333044222,15,21600,424.5,1.7857655729894502,4.9561954779584285,62.642957468606127,233.97144614524387,8519.0796956240356,4.5093971349328688E-2,0.25536678648991956,8.8669023086777626E-2,95.755804667867238,14.363370700180084,406.48339081509641,18.016609184903587,2.5163790786169784,5.2102283982242881,482.96905361664994]
[3.4003948586157833,1.0364403529060908,98,0.5,196,16,0.21252467866348645,15,21600,424.5,1.6948178286876212,4.4735650290194426,59.452597118771557,222.05545023861177,7689.498361245418,5.4926792234520613E-2,0.31029357872444019,0.10774082594598618,95.074297027256748,14.261144554088512,403.59039088070489,20.909609119295112,2.8929999343915256,6.3043763618513857,458.88756767401298]
[3.7404343444773618,1.1400843881967,98,0.5,196,16,0.23377714652983511,15,21600,424.5,1.6045664093316536,4.0334412336198877,56.286663185611005,210.23068699825711,6932.9806440520233,6.6973166378051188E-2,0.37726674510249136,0.13099539760503173,94.292638229143549,14.143895734371533,400.27224928271437,24.22775071728563,3.3181415979905182,7.6282953978401835,434.97812092200718]
[4.1144777789250986,1.25409282701637,98,0.5,196,16,0.25715486118281866,15,21600,424.5,1.5151126173266281,3.6319900716975835,53.148709261123813,198.51042909029744,6242.9363434334055,8.175864285063851E-2,0.45902538795312986,0.15938381526150341,93.398390270476767,14.009758540571516,396.47616669817393,28.023833301826073,3.7960825845404429,9.2302374313866267,411.26597368256114]
[4.5259255568176089,1.3795021097180074,98,0.5,196,16,0.28287034730110056,15,21600,424.5,1.4265700774344785,3.265741494076364,50.042721193865304,186.9095636590869,5613.4008791765846,9.9943985910817157E-2,0.55896937386394696,0.19408658814720381,92.378143062499603,13.85672145937494,392.14521730031083,32.354782699689167,4.330949397863094,11.168587291977808,387.77951809303011]
[4.97851811249937,1.5174523206898081,98,0.5,196,16,0.31115738203121063,15,21600,424.5,1.3390656294061432,2.9315580764095337,46.973148401633381,175.44470928010068,5038.9814115182071,0.12236385484419698,0.68133322870814395,0.23657403774588331,91.217593632804224,13.682639044920634,387.21868497125394,37.281315028746064,4.9265323290568972,13.513990623293154,364.55052148440643]
[5.4763699237493073,1.669197552758789,98,0.5,196,16,0.34227312023433171,15,21600,424.5,1.2527401200295392,2.6266064923675607,43.944931655758019,164.1343197342562,4514.8078071246819,0.15007796211391525,0.83141119082205917,0.28868444125765946,89.901679977039834,13.485251996555975,381.63263150253414,42.867368497465861,5.5860534687197969,16.351928654184704,341.6143494052148]
[6.0240069161242387,1.836117308034668,98,0.5,196,16,0.37650043225776492,15,21600,424.5,1.1677490366549528,2.3483314875135495,40.963525304569266,152.99876701256622,4036.4879034416231,0.18443924656832544,1.0158504373903847,0.35272584631610582,88.414782013337145,13.262217302000572,375.32074964661621,49.179250353383793,6.3118818559179317,19.785833671563523,319.01015447175502]
[6.6264076077366632,2.0197290388381348,98,0.5,196,16,0.41415047548354145,15,21600,424.5,1.0842629119648273,2.0944320490941388,38.034911472336326,142.06039434917616,3600.0665475470546,0.2271854411539185,1.2430358785443032,0.43160968005010525,86.741002900030566,13.011150435004586,368.21555731062978,56.284442689370223,7.1051923359864304,23.940858742591885,296.78101409729163]
[7.28904836851033,2.2217019427219489,98,0.5,196,16,0.45556552303189563,15,21600,424.5,1.0024674169781385,1.8628394784141307,35.165603321772601,131.34352840682067,3201.9879053079194,0.28056308638152111,1.5235989649258244,0.52902741837702238,84.864544130819709,12.729681619622957,360.2499898353297,64.2500101646703,7.9655674753000767,28.968439078536136,274.9739968282268]
[8.0179532053613638,2.4438721369941439,98,0.5,196,16,0.50112207533508524,15,21600,424.5,0.92256304679955425,1.6516970825123352,32.36263403041513,120.8744381036005,2839.0605539127037,0.34749695260709901,1.8710959175329234,0.64968608247670945,82.770186981348687,12.415528047202304,351.35944373582521,73.140556264174791,8.8905460995044905,35.051811285028748,253.64013366412826]
[8.8197485258975004,2.6882593506935581,98,0.5,196,16,0.55123428286859377,15,21600,424.5,0.84476429257926389,1.4593412117683802,29.633527743763146,110.68122612295534,2508.4248878909257,0.43182362033046012,2.3029195378633833,0.79962483953589703,80.443890632972767,12.066583594945914,341.48431573696939,83.015684263030607,9.8751279988558167,42.412691654884782,232.83426761051774]
[9.7017233784872516,2.9570852857629144,98,0.5,196,16,0.60635771115545323,15,21600,424.5,0.76929818510622361,1.284283381456933,26.986248485914643,100.79363809489119,2207.5223883025596,0.53861661861256771,2.8415361564759509,0.98664449877637184,77.873513165521175,11.681026974828177,330.57306338763738,93.926936612362624,10.911252349332017,51.319356902410647,212.61475217004283]
[10.671895716335978,3.2527938143392063,98,0.5,196,16,0.66699348227099864,15,21600,424.5,0.69640209245637752,1.1251932301313641,24.42912290316109,91.242774043306667,1934.066330332528,0.67464360244953592,3.5161797589254871,1.2208957496269053,75.049655079307172,11.257448261896075,318.58578581165892,105.91421418834108,11.987277575978453,62.096421851916887,193.04296799201822]
[11.739085287969576,3.5780731957731269,98,0.5,196,16,0.73369283049809852,15,21600,424.5,0.62632065868309716,0.98088208845538971,21.970732876160344,82.06068729245888,1686.0135401688651,0.84901606490772585,4.3651958238332131,1.5156929943865325,71.966615586372114,10.794992337955817,305.4982831641496,119.0017168358504,13.087502647509325,75.136670440819387,174.18262708110763]
[12.912993816766535,3.9358805153504401,98,0.5,196,16,0.80706211354790847,15,21600,424.5,0.5593017856205249,0.85028696141979276,19.619774565420514,73.279858001845611,1461.5368624380908,1.0741230895413305,5.4393189133745441,1.8886524004772725,68.623439220568685,10.293515883085302,291.30649949131407,133.19350050868593,14.191783672835527,90.915371233391568,156.09883653671034]
[14.204293198443191,4.3294685668854846,98,0.5,196,16,0.88776832490269941,15,21600,424.5,0.49559158868564052,0.73245476764429396,17.38488146563509,64.932532274147064,1258.9980695377778,1.3669893282817638,6.8063082416563079,2.3633014727973292,65.025014213857077,9.7537521320785618,276.03118533782333,148.46881466217667,15.27531415349074,110.00759919240375,138.85689957449353]
[15.624722518287511,4.7624154235740335,98,0.5,196,16,0.97654515739296943,15,21600,424.5,0.43542830328057669,0.62652673438531559,15.274410648073141,57.049923770553178,1076.9210386080629,1.7512748737257366,8.5575831153820445,2.9713830261743208,61.183164844121116,9.1774747266181667,259.72253476329411,164.77746523670589,16.308650574529224,133.10919502280842,122.52084141696385]
[17.187194770116264,5.2386569659314377,98,0.5,196,16,1.0741996731322665,15,21600,424.5,0.37903518363874433,0.53172291804555227,13.296193658856836,49.661283315830282,913.96514422505243,2.2602598400995642,10.817842955481609,3.7561954706533363,57.117658476146715,8.5676487714220073,242.46446023124281,182.03553976875719,17.258074532051296,161.06212597759838,107.15166229987344]
[18.905914247127892,5.7625226625245816,98,0.5,196,16,1.1816196404454933,15,21600,424.5,0.32661252208716962,0.44732690823766452,11.45725656227645,42.79285326010254,768.8989666007941,2.9413617308437199,13.759204686325329,4.7775016271962949,52.85702604733833,7.92855390710075,224.37807557095124,200.12192442904876,18.086384660291571,194.88517243289425,92.805339854777017]
[20.796505671840684,6.338774928777041,98,0.5,196,16,1.2997816044900428,15,21600,424.5,0.27832902285103123,0.3726708775170644,9.7635173420597976,36.466737272593342,640.57459394515138,3.8630758714365747,17.622280557761904,6.1188474158895501,48.43907511258422,7.265861266887633,205.62387385292001,218.87612614707999,18.754201718031226,235.81105864380174,79.530628571410205]
[22.876156239024755,6.9726524216547459,98,0.5,196,16,1.4297597649390472,15,21600,424.5,0.23431288648476506,0.30712125443910337,8.2194731516969295,30.699732221588032,527.90299624430884,5.1258095865740891,22.748090144335993,7.898642411227776,43.910961255463775,6.5866441883195659,186.40203052944372,238.09796947055628,19.221843323476293,285.33138095900063,67.366734282333582]
[25.163771862927234,7.6699176638202218,98,0.5,196,16,1.5727357414329521,15,21600,424.5,0.19464309014221154,0.25006541628257606,6.8278944346121389,25.50218571327634,429.83115171805071,6.8790833143584127,29.627173458694408,10.287213006491113,39.328681788391705,5.8993022682587561,166.95025419172279,257.54974580827718,19.451776337720901,345.25097096039076,56.340975040885617]
[27.68014904921996,8.4369094302022436,98,0.5,196,16,1.7300093155762475,15,21600,424.5,0.15934147211555144,0.20089990655331,5.5895472573199534,20.876959006090026,345.32179418316014,9.3493372305994722,38.976510689293882,13.533510656004818,34.755870983562396,5.2133806475343594,147.53867232522236,276.96132767477764,19.411581866500455,417.75367486207278,46.466573568525661]
[30.448163954141958,9.2806003732224696,98,0.5,196,16,1.9030102471338723,15,21600,424.5,0.12836633330821987,0.15902076341277491,4.5029688551820009,16.818588674104774,273.33678883271995,12.885754994804181,51.862265684098062,18.007731140311826,30.261814228156179,4.5392721342234266,128.46140139852298,296.03859860147702,19.077270926699384,505.4819465831074,37.740756234036638]
[33.492980349556156,10.208660410544717,98,0.5,196,16,2.0933112718472597,15,21600,424.5,0.10160832425777247,0.1238165799173773,3.5643233530819018,13.312747723760904,212.8252036560587,18.037344247957215,69.899609932055284,24.270697893074754,25.918664238262295,3.8877996357393441,110.02472969142345,314.47527030857657,18.436671707099549,611.63315536556092,30.143349073482323]
[36.842278384511772,11.229526451599188,98,0.5,196,16,2.3026423990319858,15,21600,424.5,7.8889369585824806E-2,9.4664781680182636E-2,2.7673640361523351,10.33610467502897,162.7169112051497,25.685476965045861,95.585086897101149,33.189266283715675,21.797913999189493,3.2696870998784235,92.532144926559383,331.9678550734406,17.492584764864034,740.07611799232791,23.636196790564959]
[40.526506222962951,12.352479096759108,98,0.5,196,16,2.5329066389351844,15,21600,424.5,5.9965096130171695E-2,7.0931825356525258E-2,2.1035185263398595,7.8566416958793743,121.9229297665311,37.277199630655559,132.86228652775671,46.132738377693308,17.966369135733387,2.6949553703600082,76.267236981188233,348.23276301881174,16.264907945371135,895.49210277071688,18.163094788939336]
[44.579156845259249,13.587727006435019,98,0.5,196,16,2.786197302828703,15,21600,424.5,4.4531423703130769E-2,5.1977131384189572E-2,1.562119979937691,5.8345181250672757,89.342183249444929,55.246385101598484,188.1086716293552,65.315510982415006,14.481854327140212,2.1722781490710319,61.475471618710202,363.02452838128977,14.791765362478031,1083.5454443525678,13.651264411264542]
[49.037072529785178,14.946499707078523,98,0.5,196,16,3.0648170331115736,15,21600,{"$f":"H75*28.3","v":424.5},3.2235082148240723E-2,{"$f":"BESSELK(G75,1)","v":3.7160902017248594E-2},1.1307760159296103,4.2234484194970943,{"$f":"(I75/(2*3.14159*O$6*D75))*(1/F75)*L75","v":63.874939407479154},83.794793615741312,271.90346524509653,94.410925432325186,11.389136546825371,1.7083704820238057,48.346884641273704,376.15311535872627,13.128586977436498,1311.0899876666081,10.013490378949424]
[{"$f":"A75*1.1","v":53.940779782763698},16.441149677786377,{"$f":"$C$10","v":98},{"$f":"$D$10","v":0.5},196,{"$f":"$F$10","v":16},3.3712987364227311,{"$f":"$H$10","v":15},21600,424.5,2.2687735825563497E-2,2.585515936131301E-2,0.7958641894974765,2.9725527477730744,44.441782839609964,{"$f":"(A76-A75)/((O75+O76)/2)*1440","v":130.38316333429918},402.28662857939571,{"$f":"Q76*500/1440","v":139.6828571456235},{"$f":"G76*BESSELK(G76,1)*100","v":8.7165466084802894},{"$f":"H75*S76/100","v":1.3074819912720435},37.00174035299883,{"$f":"J76-U76","v":387.49825964700119},11.345144288274923,1586.4188850765959,7.1514178222400284]
[59.33485776104007,18.085264645565015,98,0.5,196,16,3.7084286100650043,15,21600,424.5,1.5482802001754021E-2,1.7456998453651822E-2,0.54312196514522948,2.0285605398174322,30.006395376137512,208.66789422860529,610.954522808001,212.13698708611147,6.4738032511382952,0.97107048767074433,27.481294801082065,397.01870519891793,9.5204455519167368,1919.5668509426778,4.9596842887974191]
[65.268343537144077,19.893791110121516,98,0.5,196,16,4.0792714710715048,15,21600,424.5,1.0213595760100029E-2,1.1402677791144861E-2,0.35828322288149617,1.3381878374623881,19.599775932627193,344.48211954951375,955.43664235751476,331.74883415191482,4.651461820723787,0.69771927310856807,19.745455428972477,404.75454457102751,7.7358393721095808,2322.6758896406427,3.3305720383167392]
[71.795177890858497,21.883170221133671,98,0.5,196,16,4.4871986181786561,15,21600,424.5,6.4911232104367961E-3,7.1809148798918244E-3,0.22770242709639049,0.85046856520501846,12.343093895580218,588.46569014592535,1543.90233250344,536.07719878591672,3.2222191326309142,0.48333286989463714,13.678320218018232,410.82167978198174,6.067135210954234,2810.4378264651823,2.1587864900698235]
[78.974695679944347,24.071487243247038,98,0.5,196,16,4.9359184799965217,15,21600,424.5,3.9597510986379121E-3,4.3437320301982366E-3,0.13890430155565917,0.51880756631038705,7.4663316865251286,1043.7966081785646,2587.6989406820048,898.50657662569608,2.1440307200008286,0.3216046080001243,9.1014104064035184,415.39858959359645,4.576909811614712,3400.6297700228661,1.3459006481566904]
[86.872165247938781,26.478635967571741,98,0.5,196,16,5.4295103279961738,15,21600,424.5,2.3091719237534193E-3,2.5134522728382657E-3,8.1003554327250663E-2,0.30254827541228119,4.3203098664455375,1929.7025580701968,4517.4014987522014,1568.5421870667365,1.364681507430082,0.2047022261145123,5.7930729990406986,418.7069270009593,3.308337407362842,4114.7620217276672,0.80401670616512799]
[95.559381772732664,29.126499564328917,98,0.5,196,16,5.9724613607957915,15,21600,424.5,1.2815663924433368E-3,1.3849688724518543E-3,4.4956129869067198E-2,0.16791114506096597,2.3805881452512945,3733.7060715942616,8251.107570346463,2864.9679063702997,0.82716730766236157,0.12407509614935425,3.5113252210267252,420.98867477897329,2.2817477780139939,4978.8620462904764,0.45828700550440443]
[105.11531995000594,32.039149520761811,98,0.5,196,16,6.5697074968753713,15,21600,424.5,6.7357106799715107E-4,7.231263297471425E-4,2.362823228470785E-2,8.825144758338381E-2,1.2429636523653851,7595.0623828941834,15846.169953240646,5502.1423448752239,0.47507284697277741,7.1260927045916619E-2,2.0166842353994405,422.48331576460055,1.4946409856272567,6024.4230760114842,0.2480969491632708]
[115.62685194500655,35.243064472838,98,0.5,196,16,7.2266782465629094,15,21600,424.5,3.3344916064321578E-4,3.5581346383584144E-4,1.169707933900167E-2,4.3688591331171228E-2,0.61159880974714842,16323.641162841997,32169.811116082645,11170.073304195363,0.25713494189366737,3.8570241284050108E-2,1.0915378283386181,423.40846217166137,0.92514640706082218,7289.5519219739072,0.12691402941681848]
[127.18953713950721,38.767370920121799,98,0.5,196,16,7.9493460712192006,15,21600,424.5,1.5455750745955562E-4,1.6400559486098388E-4,5.421730328261801E-3,2.0250162776057828E-2,0.28190509017704823,37269.60046059906,69439.411576681712,24110.906797458931,0.13037372311661299,1.9556058467491949E-2,0.55343645463002222,423.94656354537,0.53810137370862776,8820.3578255884058,6.1006751012704072E-2]
[139.90849085345795,42.644108012133984,98,0.5,196,16,8.7442806783411218,15,21600,424.5,6.6637028971335279E-5,7.0349061360512429E-5,2.3375635832745953E-3,8.730799983530612E-3,0.12092123139772126,90933.945311662173,160373.35688834387,55685.193364008286,6.1515193799416279E-2,9.2272790699124418E-3,0.26113199767852213,424.23886800232145,0.2923044569514559,10672.632968961989,2.7388223487262411E-2]
[153.89933993880376,46.908518813347392,98,0.5,196,16,9.6187087461752352,15,21600,424.5,2.6532087018184206E-5,2.7878659097686191E-5,9.3072037213212016E-4,3.4762405899134686E-3,4.7919925619672031E-2,238648.2423929674,399021.59928131127,138549.16641712197,2.6815670209455196E-2,4.0223505314182792E-3,0.11383252003913731,424.38616747996087,0.14729947763942164,12913.885892444006,1.1406286137746306E-2]
[169.28927393268415,51.599370694682129,98,0.5,196,16,10.58057962079276,15,21600,424.5,9.6785124955288195E-6,1.0125972117820742E-5,3.3951301099495804E-4,1.2680810960661684E-3,1.7405278676158254E-2,678497.83831758588,1077519.4375988971,374138.69361072819,1.0713865423052985E-2,1.6070798134579479E-3,4.5480358720859926E-2,424.45451964127915,6.8352161318273374E-2,15625.801929857247,4.3743138192266729E-3]
[186.21820132595258,56.75930776415035,98,0.5,196,16,11.638637582872036,15,21600,424.5,3.2065124111987511E-6,3.3415315214399603E-6,1.1248140497020754E-4,4.2011804756372513E-4,5.7436744501274152E-3,2106156.1888624388,3183675.6264613359,1105442.9258546305,3.8890874349782694E-3,5.8336311524674047E-4,1.6509176161482755E-2,424.48349082383851,2.8971182559359931E-2,18907.220335127276,1.5322814271929257E-3]
[204.84002145854785,62.435238540565386,98,0.5,196,16,12.802501341159241,15,21600,424.5,9.5558663113790576E-7,9.9222906678806822E-7,3.3521069953057086E-5,1.2520119627466823E-4,1.7055175757038853E-3,7199551.5481277183,10383227.174589055,3605287.2133989772,1.2703013958291426E-3,1.9054520937437141E-4,5.3924294252947107E-3,424.49460757057471,1.1116746736206551E-2,22877.736605503989,4.8591986733215788E-4]
[225.32402360440267,68.678762394621941,98,0.5,196,16,14.082751475275167,15,21600,424.5,2.5347073089541955E-7,2.6232053224437616E-7,8.8915121084104787E-6,3.3209797724913138E-5,4.5089616217254048E-4,27357424.572038472,37740651.746627524,13104392.967579002,3.6941948624594553E-4,5.5412922936891833E-5,1.5681857191140389E-3,424.49843181428088,3.8242437061626333E-3,27682.061292659899,1.3814880567353775E-4]
[247.85642596484297,75.546638634084147,98,0.5,196,16,15.491026622802686,15,21600,424.5,5.9149933133819498E-8,6.1030095110971426E-8,2.0749233839074806E-6,7.7498388388944401E-6,1.0490309480207339E-4,116756757.01925609,154497408.76588362,53644933.599265151,9.4541882815623842E-5,1.4181282422343577E-5,4.0133029255232322E-4,424.49959866970744,1.1668554265611419E-3,33495.294164118444,3.48363988339331E-5]
[272.64206856132728,83.101302497492554,98,0.5,196,16,17.040129285082955,15,21600,424.5,1.1989244525623014E-8,1.2336153984987742E-8,4.20571292368485E-7,1.5708337769962914E-6,2.1204304673408629E-5,566046488.74512017,720543897.51100373,250188853.30243188,2.1020965878488243E-5,3.153144881773236E-6,8.9234000154182581E-5,424.49991076599986,3.1209629241857328E-4,40529.305938583275,7.7005091794938047E-6]
[299.90627541746005,91.411432747241832,98,0.5,196,16,18.744142213591253,15,21600,424.5,2.081261942878851E-9,2.1360752886380317E-9,7.3008689013156737E-8,2.726874534641404E-7,3.6716460641412063E-6,3156499085.1640644,3877042982.6750679,1346195480.0955098,4.0038898989169253E-6,6.005834848375388E-7,1.6996512620902349E-5,424.49998300348739,7.2237487529491773E-5,49040.460185685894,1.4730181416726735E-6]
[329.8969029592061,100.55257602196602,98,0.5,196,16,20.618556434950381,15,21600,424.5,3.0467267398996493E-10,3.1197538184858508E-10,1.0687627562810353E-8,3.9918288947096668E-8,5.3624663370534013E-7,20526428196.334793,24403471179.009861,8473427492.7117567,6.4324820169602463E-7,9.6487230254403695E-8,2.7305886161996244E-6,424.49999726941138,1.4265923994116747E-5,59338.956824679859,2.4041413529169696E-7]
[362.88659325512674,110.60783362416264,98,0.5,196,16,22.680412078445421,15,21600,424.5,3.6975465165113674E-11,3.7781983019176889E-11,1.2970641425473526E-9,4.8445345724143623E-9,6.4942499913596367E-8,158037300974.36139,182440772153.37125,63347490331.031685,8.5691094401575931E-8,1.285366416023639E-8,3.6375869573468986E-7,424.49999963624128,2.3668299036216922E-6,71800.137757862685,3.2964141539721564E-8]
[399.17525258063944,121.66861698657891,98,0.5,196,16,24.948453286289965,15,21600,424.5,3.6511402871259757E-12,3.7236074182597732E-12,1.2807852787500124E-10,4.7837330161312957E-10,6.4004150950960426E-9,1464915455791.832,1647356227945.2034,571998690258.7511,9.289824573093672E-9,1.3934736859640508E-9,3.9435305312782636E-8,424.49999996056471,3.2432342322863406E-7,86878.166687013698,3.7330831852960013E-9]
[439.0927778387034,133.83547868523681,98,0.5,196,16,27.443298614918962,15,21600,424.5,2.8735932023446165E-13,2.9254869876878094E-13,1.0080291583581387E-11,3.7649889064676478E-11,5.0285459698796386E-10,16653336443606.123,18300692671551.328,6354407177621.9893,8.0285012997176309E-10,1.2042751949576446E-10,3.4080988017301342E-9,424.4999999965919,3.6027188343723537E-8,105122.58169128676,3.4271597751969693E-10]
[{"$f":"A98*1.1","v":483.00205562257378},147.2190265537605,98,0.5,196,16,30.187628476410861,15,21600,424.5,1.7622013364735423E-14,1.7911541795409864E-14,6.1816346468722704E-13,2.308840540606793E-12,3.0787698488731271E-11,236972820725506.62,255273513397057.94,88636636596200.672,5.4070696915953812E-11,8.1106045373930728E-12,2.2953010840822396E-10,424.49999999977047,3.1785702958586626E-9,127198.32384645683,2.4989089476490009E-11]
[{"$f":"A99*1.1","v":531.3022611848312},161.94092920913656,98,0.5,196,16,33.20639132405195,15,21600,424.5,8.2126949565238553E-16,{"$f":"BESSELK(G100,1)","v":8.3354495428698642E-16},2.8809352618603715E-14,1.0760293203048487E-13,1.4327594476522166E-12,4317275449466030.5,4572548962863088,{"$f":"Q100*500/1440","v":1587690612105239},{"$f":"G100*BESSELK(G100,1)*100","v":2.7679019938242666E-12},4.1518529907363999E-13,1.1749743963784012E-11,424.49999999998823,2.177671376557555E-10,153909.97185421293,1.4148994703347069E-12]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,"Effective Porosity, n = ",null,{"$f":"'Tab 2   Inputs and Plots'!R37","v":0.25}]
[{"$f":"'Tab 2   Inputs and Plots'!M37","v":"Lower Bound"}]
["Radius, r",null,"Transmissivity, T","Thickness, b","Conductivity, K","Leakance, B","r/B","Flow Rate, Qw",null,null,"Ko(r/B)","K1(r/B)","Vacuum",null,"Velocity","Travel Time","Cummulative Travel Time","Time for 500 Pore Volumes","Q(r)/Qw","Qr","Qr","Qleak","Delta Q","Delta A","Qleak/A"]
["(ft)","(m)","(ft2/d)","(ft)","(ft/d)","B (ft)","(dim)","(ft3/min)","(ft3/day)","(L/min)","(dim)","(dim)","(ft-air)","(Pa)","(ft/day)","(min)","(min)","(days)","(%)","(scfm)","(L/min)","(L/min)","(L/min)","(ft2)","(L/min per 1000 ft2)"]
[0.1,{"$f":"A108*0.3048","v":3.0480000000000004E-2},{"$f":"'Tab 2   Inputs and Plots'!O37","v":32},{"$f":"'Tab 2   Inputs and Plots'!Q37","v":0.5},{"$f":"C108/D108","v":64},{"$f":"'Tab 2   Inputs and Plots'!$P$37","v":4},{"$f":"(A108/F108)","v":2.5000000000000001E-2},{"$f":"'Tab 2   Inputs and Plots'!$N$37","v":15},{"$f":"(H108*1440)","v":21600},{"$f":"H108*28.3","v":424.5},{"$f":"BESSELK(G108,0)","v":3.8055617583367658},{"$f":"BESSELK(G108,1)","v":39.94618492708868},{"$f":"(I108*K108/(2*3.1459*C108))","v":408.27015907646728},{"$f":"(M108*0.015)*249","v":1524.8890441506053},{"$f":"(I108/(2*3.14159*O$104*D108))*(1/F108)*L108","v":274649.96846345818}]
[{"$f":"A108*1.1","v":0.11000000000000001},{"$f":"A109*0.3048","v":3.3528000000000009E-2},{"$f":"$C$108","v":32},{"$f":"$D$108","v":0.5},{"$f":"C109/D109","v":64},{"$f":"$F$108","v":4},{"$f":"(A109/F109)","v":2.7500000000000004E-2},{"$f":"$H$108","v":15},21600,{"$f":"H109*28.3","v":424.5},{"$f":"BESSELK(G109,0)","v":3.7103912309074829},{"$f":"BESSELK(G109,1)","v":36.305749281929408},{"$f":"(I109*K109/(2*3.1459*C109))","v":398.06002747426032},{"$f":"(M109*0.015)*249","v":1486.7542026163621},{"$f":"(I109/(2*3.14159*O$104*D109))*(1/F109)*L109","v":249620.15555488633},{"$f":"(A109-A108)/((O108+O109)/2)*1440","v":5.4933513623202947E-5},{"$f":"P109","v":5.4933513623202947E-5},{"$f":"Q109*500/1440","v":1.9074136674723243E-5},{"$f":"G109*BESSELK(G109,1)*100","v":99.840810525305884},{"$f":"H108*S109/100","v":14.976121578795883},{"$f":"T109*28.3","v":423.82424067992349},{"$f":"J109-U109","v":0.67575932007650863},null,{"$f":"(3.14159*A109*A109)-(3.14159*A108*A108)","v":6.5973390000000007E-3}]
[{"$f":"A109*1.1","v":0.12100000000000002},3.6880800000000012E-2,{"$f":"$C$108","v":32},{"$f":"$D$108","v":0.5},64,{"$f":"$F$108","v":4},3.0250000000000006E-2,{"$f":"$H$108","v":15},21600,424.5,3.615246249574076,32.995615691931242,387.85263652094812,1448.6295974057412,226861.3342115664,6.6487367674089446E-5,{"$f":"Q109+(P110)","v":1.214208812972924E-4},{"$f":"Q110*500/1440","v":4.2160028228226529E-5},{"$f":"G110*BESSELK(G110,1)*100","v":99.811737468092034},{"$f":"H109*S110/100","v":14.971760620213804},423.70082555205067,{"$f":"J110-U110","v":0.79917444794932635},{"$f":"V110-V109","v":0.12341512787281772},7.9827801900000106E-3,{"$f":"1000*W110/X110","v":15460.168629899048}]
[0.13310000000000002,4.0568880000000009E-2,32,0.5,64,4,3.3275000000000006E-2,15,21600,424.5,3.5201313857415575,29.985716932047502,377.64847664826465,1410.5170602812684,206166.7772472621,8.0475144864384355E-5,{"$f":"Q110+(P111)","v":2.0189602616167674E-4},7.0102786861693316E-5,99.777473091388075,14.966620963708211,423.5553732729424,0.94462672705759587,{"$f":"V111-V110","v":0.14545227910826952},9.6591640299000039E-3,{"$f":"1000*W111/X111","v":15058.474900935636}]
[0.14641000000000004,4.4625768000000017E-2,32,0.5,64,4,3.660250000000001E-2,15,21600,424.5,3.4250520045283155,27.248717650800089,367.44812343949474,1372.4187410465129,187348.54047067949,9.7411201734911104E-5,2.9930722789658784E-4,1.0392612079742635E-4,99.737118781341053,14.960567817201159,423.3840692267928,1.1159307732071966,0.17130404614960071,1.1687588476179019E-2,14656.919731452123]
[0.16105100000000006,4.9088344800000017E-2,32,0.5,64,4,4.0262750000000014E-2,15,21600,424.5,3.3300143966570204,24.759766106719564,357.2522517790598,1334.3371603947883,170235.75574952256,1.1791927231064413E-4,4.1722650020723201E-4,1.4487031257195556E-4,99.689627281332349,14.953444092199852,423.18246780925585,1.3175321907441457,0.20160141753694916,1.4141982056176602E-2,14255.527742583892]
[0.17715610000000007,5.3997179280000022E-2,32,0.5,64,4,4.4289025000000017E-2,15,21600,424.5,3.2350259307919047,22.49626850501933,347.06165219564122,1296.2752709507199,154673.07946244339,1.4275600714194373E-4,5.5998250734917579E-4,1.9443837060735271E-4,99.633779822551418,14.945066973382714,422.94539534673083,1.5546046532691662,0.23707246252502046,1.7111798287973698E-2,13854.327788075716]
[0.19487171000000009,5.9396897208000031E-2,32,0.5,64,4,4.8717927500000022E-2,15,21600,424.5,3.1400952291164987,20.437683884652795,336.87724969859767,1258.2365276242622,140519.28224513715,1.7283969173478056E-4,7.328221990839563E-4,2.5445215245970703E-4,99.568160176043364,14.935224026406503,422.66683994730408,1.8331600526959164,0.27855539942675023,2.0705275928448161E-2,13453.35364712658]
[0.21435888100000011,6.5336586928800039E-2,32,0.5,64,4,5.3589720250000028E-2,15,21600,424.5,3.0452323692271874,18.565337692733895,326.70012543760947,1220.2249685094714,127645.96722139177,2.0928532907096557E-4,9.4210752815492189E-4,3.2712066949823677E-4,99.49112533003904,14.923668799505856,422.33982702601577,2.1601729739842312,0.32701292128831483,2.5053383873422291E-2,13052.644821972501]
[0.23579476910000013,7.187024562168004E-2,32,0.5,64,4,5.8948692275000034E-2,15,21600,424.5,2.950449115698059,16.86225235315775,316.5315415455338,1182.2453076725687,115936.40507774962,2.5344755921903665E-4,1.1955550873739586E-3,4.1512329422706897E-4,99.400772502969133,14.910115875445369,421.95627927510395,2.5437207248960476,0.38354775091181637,3.0314594486840984E-2,12652.247453889166]
[0.25937424601000014,7.9057270183848047E-2,32,0.5,64,4,6.4843561502500036E-2,15,21600,424.5,2.855759184940041,15.312993290669471,306.37296955315293,1144.303041281026,105284.47540209276,3.0697325385154085E-4,1.5025283412254994E-3,5.2171122959218728E-4,99.294902223089636,14.894235333463445,421.50685993701552,2.9931400629844802,0.4494193380884326,3.6680659329077575E-2,12252.215372043978]
[0.28531167061100016,8.6962997202232856E-2,32,0.5,64,4,7.1327917652750039E-2,15,21600,424.5,2.7611785472167587,13.903529011981767,296.22612279018915,1106.4045686213565,95593.704671458152,3.7186608731485402E-4,1.8743944285403535E-3,6.5083139879873388E-4,99.170977244925666,14.875646586738849,420.98079840470945,3.5192015952905535,0.52606153230607333,4.4383597788183848E-2,11852.611291600286]
[0.31384283767210019,9.5659296922456144E-2,32,0.5,64,4,7.8460709418025049E-2,15,21600,424.5,2.6667257698702977,12.621103973091495,286.09299320742093,1068.5573296297171,86776.392151355307,4.5056597856501851E-4,2.324960407105372E-3,8.0727791913380977E-4,99.026077136741321,14.853911570511197,420.36569744546688,4.1343025545331216,0.61510095924256802,5.3704153323702486E-2,11453.508177198864]
[0.34522712143931022,0.10522522661470177,32,0.5,64,4,8.6306780359827556E-2,15,21600,424.5,2.572422405925213,11.454123077823873,275.97589306709028,1030.7699606055824,78752.815765582287,5.4604705953115455E-4,2.8710074666365264E-3,9.9687759258212721E-4,98.856848469217695,14.828527270382654,419.64732175182911,4.8526782481708892,0.71837569363776765,6.4982025521680087E-2,11054.990789692982]
[0.37974983358324127,0.11574774927617194,32,0.5,{"$f":"C122/D122","v":64},4,{"$f":"(A122/F122)","v":9.4937458395810317E-2},15,{"$f":"(H122*1440)","v":21600},424.5,2.4782934322441341,10.392046757863088,265.87750194932937,993.05246978074513,71450.510719044411,6.6193880855693033E-4,3.5329462751934569E-3,1.2267174566643947E-3,98.659450672194254,14.798917600829139,418.80936810346464,5.6906318965353648,0.83795364836447561,7.862825088123282E-2,10657.157433531062]
[0.41772481694156544,0.12732252420378914,32,0.5,64,4,0.10443120423539136,15,21600,424.5,2.3843677412596973,9.4252956800270358,255.80091950638857,955.41643435636126,64803.614312683705,8.0267626427094356E-4,4.3356225394644001E-3,1.5054244928695835E-3,98.42949781398552,14.764424672097828,417.83321822036856,6.6667817796314353,0.97614988309607043,9.5140183566291725E-2,10260.121922257058]
[0.45949729863572203,0.14005477662416807,32,0.5,64,4,0.11487432465893051,15,21600,424.5,2.2906786899510574,8.5451642131341732,245.74972435820649,917.87522047790117,58752.270984978357,9.7368690280791846E-4,5.3093094422723185E-3,1.8435102230112215E-3,98.161996808344938,14.724299521251742,416.69767645142434,7.8023235485756572,1.135541768944222,0.11511962211521309,9864.0157783679842]
[0.50544702849929424,0.1540602542865849,32,0.5,64,4,0.12636175712482356,15,21600,424.5,2.197264709102686,7.7437418652246883,235.7280394552136,880.44422736522267,53242.092153607977,1.1816239522995547E-3,6.4909333945718734E-3,2.253796317559678E-3,97.851282881085027,14.677692432162752,415.37869583020591,9.1213041697940866,1.3189806212184294,0.13929474275940779,9468.990681842135]
[0.55599173134922375,0.16946627971524342,32,0.5,64,4,0.13899793283730594,15,21600,424.5,2.1041699748988023,7.0138419727865671,225.74060412865816,843.14115642053821,48223.665918273822,1.4346588146975762E-3,7.9255922092694494E-3,2.7519417393296699E-3,97.490953546486452,14.623643031972968,413.84909780483503,10.650902195164974,1.5295980253708876,0.16854663873888365,9075.2211780418602]
[0.61159090448414621,{"$f":"A127*0.3048","v":0.18641290768676777},32,0.5,64,4,0.15289772612103655,15,21600,424.5,{"$f":"BESSELK(G127,0)","v":2.0114451434742158},6.3489369875722215,{"$f":"(I127*K127/(2*3.1459*C127))","v":215.79285289505319},{"$f":"(M127*0.015)*249","v":805.98630556302362},43652.112125248677,1.7428491169100473E-3,{"$f":"Q126+(P127)","v":9.6684413261794964E-3},3.3570976827012144E-3,97.073802868553642,14.561070430283046,412.07829317701021,12.42170682298979,1.7708046278248162,0.2039414328740492,8682.9076508373619]
[0.67274999493256094,{"$f":"A128*0.3048","v":0.20505419845544459},32,0.5,64,4,0.16818749873314023,15,21600,424.5,{"$f":"BESSELK(G128,0)","v":1.9191481470524523},5.7430997640753016,{"$f":"(I128*K128/(2*3.1459*C128))","v":205.89100086786058},{"$f":"(M128*0.015)*249","v":769.00288824145923},39486.678689461871,2.1186040687552143E-3,{"$f":"Q127+(P128)","v":1.1787045394934711E-2},4.0927240954634417E-3,96.59175842947127,14.488763764420691,410.03201453310555,14.467985466894447,2.0462786439046567,0.24676913377759946,8292.2795593587653]
[0.74002499442581704,{"$f":"A129*0.3048","v":0.22555961830098906},32,0.5,64,4,0.18500624860645426,15,21600,424.5,{"$f":"BESSELK(G129,0)","v":1.8273450476310811},5.1909503022070753,{"$f":"(I129*K129/(2*3.1459*C129))","v":196.04213534298287},{"$f":"(M129*0.015)*249","v":732.21737550604098},35690.37542380541,2.5772757502396481E-3,{"$f":"Q128+(P129)","v":1.436432114517436E-2},4.9876115087410973E-3,96.035824211387094,14.405373631708065,407.67207377733826,16.827926222661745,2.3599407557672976,0.29859065187089562,7903.5989270946329]
[0.81402749386839879,{"$f":"A130*0.3048","v":0.24811558013108798},32,0.5,64,4,0.2035068734670997,15,21600,424.5,{"$f":"BESSELK(G130,0)","v":1.7361109406868458},4.6876074455475649,{"$f":"(I130*K130/(2*3.1459*C130))","v":186.25431275050394},{"$f":"(M130*0.015)*249","v":695.65985812313215},32229.641940491092,3.1379143684770305E-3,{"$f":"Q129+(P130)","v":1.750223551365139E-2},6.0771651089067324E-3,95.396033528448271,14.309405029267241,404.95616232826291,19.543837671737094,2.7159114490753495,0.36129468876378312,7517.1640589796507]
[0.89543024325523879,{"$f":"A131*0.3048","v":0.27292713814419678},32,0.5,64,4,0.2238575608138097,15,21600,424.5,{"$f":"BESSELK(G131,0)","v":1.645530896926652},4.2286450760808441,{"$f":"(I131*K131/(2*3.1459*C131))","v":176.53665968808451},{"$f":"(M131*0.015)*249","v":659.36442393499567},29074.046467981578,3.8242383830480531E-3,{"$f":"Q130+(P131)","v":2.1326473896699442E-2},7.4050256585761953E-3,94.661417227878459,14.199212584181769,401.83771613234404,22.662283867655958,3.1184461959188639,0.43716657340417875,7133.3134453437042]
[0.98497326758076276,{"$f":"A132*0.3048","v":0.3002198519586165},32,0.5,{"$f":"C132/D132","v":64},4,{"$f":"(A132/F132)","v":0.24624331689519069},15,{"$f":"(H132*1440)","v":21600},424.5,{"$f":"BESSELK(G132,0)","v":1.5557009245629172},3.810052381852671,{"$f":"(I132*K132/(2*3.1459*C132))","v":166.89947615626195},{"$f":"(M132*0.015)*249","v":623.36954344363835},26196.012671296288,4.6658880788901288E-3,{"$f":"Q131+(P132)","v":2.5992361975589573E-2},9.0251256859686015E-3,93.819993605182333,14.072999040777349,398.26587285399899,26.234127146001015,3.5718432783450567,0.52897155381905536,6752.4297905192698]
[1.0834705943388392,0.33024183715447819,32,0.5,64,4,0.2708676485847098,15,21600,424.5,1.4667289278148088,3.4281978047885624,157.35433838885467,587.71845388237216,23570.571775258057,5.7000556541689793E-3,3.1692417629758551E-2,1.1004311676999497E-2,92.858787826634199,13.928818173995131,394.1855543240622,30.314445675937804,4.0803185299367897,0.64005558012105812,6374.9440777706386]
[1.1918176537727232,0.36326602086992604,32,0.5,64,4,0.2979544134431808,15,21600,424.5,1.3787356292340327,3.0797963022574875,147.91419780237325,552.45952879186405,21175.13747139561,6.97361906701528E-3,3.8666036696773834E-2,1.3425707186379804E-2,91.763890076360681,13.764583511454102,389.53771337415111,34.96228662584889,4.6478409499110853,0.77446725194648014,6001.3395508068261]
[1.3109994191499956,0.39959262295691866,32,0.5,64,4,0.32774985478749891,15,21600,424.5,1.2918554139864622,2.7618795781646548,138.59347157265995,517.64661632388493,18989.301241841407,8.5459549612334467E-3,4.7211991658007282E-2,1.6393052659030308E-2,90.520563068402438,13.578084460260365,384.25979022536836,40.240209774631637,5.2779231487827474,0.93710537485523915,5632.1554548740723]
[1.4420993610649953,0.43955188525261057,32,0.5,64,4,0.36052484026624881,15,21600,424.5,1.2062370434428162,2.4717689577706881,129.4081191906769,483.33932517717818,16994.645860168534,1.0492674181763379E-2,5.7704665839770658E-2,2.0036342305475921E-2,89.113410867534952,13.367011630130243,378.2864291326859,46.213570867314104,5.9733610926824667,1.1338975035748424,5267.9903376189041]
[1.5863092971714949,0.48350707377787167,32,0.5,64,4,0.39657732429287373,15,21600,424.5,1.1220441735335926,2.2070505955324276,120.37569807291634,449.60323230234252,15174.574932916275,1.2910620952186647E-2,7.0615286791957305E-2,2.4519196802762953E-2,87.526621975524364,13.128993296328654,371.55051028610092,52.949489713899084,6.7359188465849797,1.3720159793255577,4909.5046618160804]
[1.7449402268886445,0.53185778115565885,32,0.5,64,4,0.43623505672216112,15,21600,424.5,1.0394556006884348,1.9655527176651719,111.51538994638949,416.50998144976472,13514.156430841618,1.5924617641424617E-2,8.6539904433381915E-2,3.004857792825761E-2,85.744300128106417,12.861645019215961,363.98455404381173,60.515445956188273,7.5659562422891895,1.660139334983926,4557.4224300651522]
[1.919434249577509,0.58504355927122476,32,0.5,64,4,0.47985856239437724,15,21600,424.5,0.95866514544716752,1.7453246116724532,102.84798836212818,384.13723653254874,11999.978231444904,1.9696642351220268E-2,0.10623654678460218,3.6887689855764648E-2,83.750895906866816,12.562634386030021,355.52255312464962,68.977446875350381,8.4620009191621079,2.0087685953305474,4212.5314677023152]
[2.1113776745352602,0.64354791519834731,32,0.5,64,4,0.52784441863381504,15,21600,424.5,0.87988107196530474,1.5446170848867322,94.395836418287402,352.56844902230341,10620.013761679093,2.443842880432328E-2,0.13067497558892546,4.5373255412821341E-2,81.531750718389532,12.229762607758429,346.10228179956357,78.397718200436429,9.4202713250860484,2.4306100003499669,3875.6819579157859]
[2.3225154419887866,0.70790270671818223,32,0.5,64,4,0.58062886049719664,15,21600,424.5,0.80332493200472677,1.3618641245559726,86.182702740581476,321.89239473607176,9363.4959018869467,3.0428927676042935E-2,0.1611039032649684,5.5938855300336252E-2,79.073761479294674,11.861064221894202,335.66811747960594,88.831882520394061,10.434164319957631,2.9410381004234623,3547.7827772633341]
[2.5547669861876656,{"$f":"A142*0.3048","v":0.77869297739000054},32,0.5,{"$f":"C142/D142","v":64},4,{"$f":"(A142/F142)","v":0.63869174654691641},15,{"$f":"(H142*1440)","v":21600},424.5,{"$f":"BESSELK(G142,0)","v":0.72922971642099543},1.1956655050200165,{"$f":"(I142*K142/(2*3.1459*C142))","v":78.233583169231679},{"$f":"(M142*0.015)*249","v":292.20243313708028},8220.7974014535175,3.8038744904562341E-2,{"$f":"Q141+(P142)","v":0.19914264816953076},6.9146752836642622E-2,76.366168968713509,11.454925345307027,{"$f":"T142*28.3","v":324.17438727218888},100.32561272781112,{"$f":"V142-V141","v":11.493730207417059},{"$f":"(3.14159*A142*A142)-(3.14159*A141*A141)","v":3.5586561015123905},{"$f":"1000*W142/X142","v":3229.795147255827}]
[2.8102436848064323,0.85656227512900063,32,0.5,64,4,0.70256092120160807,15,21600,424.5,0.65783719793951045,1.0447701052668332,70.574415685363419,263.59544258483237,7183.3161786750024,4.7764701824271366E-2,0.24690734999380212,8.5731718747847963E-2,73.401464760016751,11.010219714002512,311.58921790627107,112.91078209372893,12.585169365917807,4.3059738828299849,2922.7231071003489]
[3.0912680532870755,0.94221850264190066,32,0.5,64,4,0.77281701332176889,15,21600,424.5,0.58939435892348435,0.90805972522209299,63.231697173043003,236.17038894131559,6243.3640496682283,6.0279247547412658E-2,0.3071865975412148,0.10666201303514403,70.176400476392402,10.52646007145886,297.89882002228575,126.60117997771425,13.690397883985327,5.2102283982242881,2627.6003348819004]
[3.4003948586157833,1.0364403529060908,32,0.5,64,4,0.85009871465394582,15,21600,424.5,0.52414882000024732,0.78453322432801698,56.231992990903549,210.02649382102476,5394.0576731798765,7.6501928051533469E-2,0.38368852559274824,0.13322518249748203,66.693068560456297,10.003960284068445,283.11207603913698,141.38792396086302,14.786743983148767,6.3043763618513857,2345.4729119005824]
[3.7404343444773618,1.1400843881967,32,0.5,64,4,0.93510858611934045,15,21600,424.5,0.46234322306744036,0.67329085413750311,49.601334367036813,185.2609838608825,4629.2108293475812,9.7704029282903407E-2,0.48139255487565163,0.16715019266515682,62.960005865960369,9.4440008798940553,267.26522490100177,157.23477509899823,15.846851138135207,7.6282953978401835,2077.3777510794826]
[4.1144777789250986,1.25409282701637,32,0.5,64,4,1.0286194447312746,15,21600,424.5,0.40420857829543894,0.57351872023390971,43.364504648816123,161.96642486332823,3943.2275876395233,0.12566378885555107,0.60705634373120265,0.21078345268444537,58.993250754999551,8.8489876132499337,250.42634945497312,174.07365054502688,16.838875446028652,9.2302374313866267,1824.3166084514257]
[4.5259255568176089,1.3795021097180074,32,0.5,64,4,1.1314813892044022,15,21600,424.5,0.34995666131777875,0.48447338928329825,37.544223654518682,140.22767534962728,3330.9964726521421,0.16289979391738965,0.76995613764859228,0.26734588112798341,54.817262353883144,8.222589353082471,232.69927869223395,191.80072130776605,17.727070762739174,11.168587291977808,1587.225877302513]
[4.97851811249937,1.5174523206898081,32,0.5,64,4,1.2446295281248425,15,21600,424.5,0.29977164413909718,0.40546675422820239,32.160249816251408,120.118533063699,2787.7864047597468,0.21302709811380166,0.98298323576239399,0.341313623528609,50.465589498535898,7.5698384247803849,214.22642742128491,210.27357257871509,18.472851270949036,13.513990623293154,1366.9427326010295]
[5.4763699237493073,1.669197552758789,32,0.5,64,4,1.3690924809373268,15,21600,424.5,0.25380125884371801,0.33585138172244094,27.228432200564171,101.69819426910718,2309.1459564121114,0.28130905313214027,1.2642922888945343,0.43899037808837998,45.981160142860581,6.8971740214290866,195.19002480644315,229.30997519355685,19.036402614841762,16.351928654184704,1164.1686444106433]
[6.0240069161242387,1.836117308034668,32,0.5,64,4,1.5060017290310597,15,21600,424.5,0.21214792043361574,0.27500668448467885,22.759758144361015,85.007696669188391,1890.808280160385,0.37552660081527961,1.6398188897098138,0.56938155892701869,41.416054232902546,6.2124081349353819,175.81115021867132,248.68884978132868,19.378874587771833,19.785833671563523,979.43179496264645]
[6.6264076077366632,2.0197290388381348,32,0.5,64,4,1.6566019019341658,15,21600,424.5,0.17486036285661821,0.2223263764674959,18.759455947140292,70.066567962568982,1528.604856680188,0.50737185663583984,2.1471907463456539,0.74555234248112978,36.830629810618504,5.5245944715927759,156.34602354607557,268.15397645392443,19.465126672595744,23.940858742591885,813.0504791779415]
[7.28904836851033,2.2217019427219489,32,0.5,64,4,1.8222620921275825,15,21600,424.5,0.14192645627894598,0.17720776486258327,15.22622429007415,56.869947723426947,1218.3918719603128,0.69472430423047415,2.8419150505761279,0.9867760592278223,32.29189923397437,4.8437848850961549,137.07911224822118,287.42088775177882,19.266911297854392,28.968439078536136,665.10008515198217]
[8.0179532053613638,2.4438721369941439,32,0.5,64,4,2.0044883013403409,15,21600,424.5,0.11326795899126066,0.1390434925198652,12.151669207397079,45.386484489628089,955.99344231076896,0.96544339053113348,3.8073584411072616,1.3219994587177992,27.871105413357299,4.1806658120035944,118.31284247970173,306.18715752029829,18.766269768519464,35.051811285028748,535.38659146367343]
[8.8197485258975004,2.6882593506935581,32,0.5,64,4,2.2049371314743751,15,21600,424.5,8.8737981861880769E-2,0.107216294582545,9.5200320666215585,35.557319768831519,737.16556361045593,1.3638237844576711,5.1711822255649329,1.7955493838767129,23.640518902414836,3.5460778353622255,100.35400274075099,324.14599725924904,17.958839738950758,42.412691654884782,423.430794845165]
[9.7017233784872516,2.9570852857629144,32,0.5,64,4,2.4254308446218129,15,21600,424.5,6.8121749317676228E-2,8.1097346279811786E-2,7.308271208466806,27.296392963623518,557.5847515569933,1.9618358425577798,7.1330180681227127,2.4767423847648309,19.669600508403153,2.950440076260473,83.497454158171394,341.00254584182858,16.856548582579535,51.319356902410647,328.4637532507295]
[10.671895716335978,3.2527938143392063,32,0.5,64,4,2.6679739290839946,15,21600,424.5,5.1141271054300642E-2,6.0048529005920913E-2,5.4865631395869121,20.492313326357117,412.86362209196358,2.8791808084528245,10.012198876575537,3.476457943255395,16.020790986764101,2.4031186480146154,68.008257738813612,356.4917422611864,15.489196419357825,62.096421851916887,249.43782519861375]
[11.739085287969576,3.5780731957731269,32,0.5,64,4,2.9347713219923941,15,21600,424.5,3.7464105024432884E-2,4.3428494911783473E-2,4.0192426478101968,15.011871289571085,298.59258849643749,4.3200212754666341,14.332220152042172,4.976465330570198,12.745270142439475,1.9117905213659214,54.103671754655579,370.39632824534442,13.904585984158018,75.136670440819387,185.05725503380964]
[12.912993816766535,3.9358805153504401,32,0.5,64,4,3.2282484541916339,15,21600,424.5,2.6715917090306993E-2,3.0602351220567096E-2,2.8661502329948854,10.705071120235896,210.40644589658399,6.6421669482475441,20.974387100289718,7.2827732987117075,9.8791993022425189,1.4818798953363779,41.937201038019495,382.56279896198049,12.16647071663607,90.915371233391568,133.8219329864821]
[14.204293198443191,4.3294685668854846,32,0.5,64,4,3.5510732996107977,15,21600,424.5,1.8496219280214381E-2,2.0954054213223848E-2,1.9843205464485056,7.4114372409851681,144.06958610309911,10.491378495322618,31.465765595612336,10.925613054032061,7.4409382435176346,1.1161407365276452,31.586782843732362,392.91321715626765,10.350418194287158,110.00759919240375,94.088210907904951]
[15.624722518287511,4.7624154235740335,32,0.5,64,4,3.9061806295718777,15,21600,424.5,1.2396104590843818E-2,1.3900310528214201E-2,1.3298850247655005,4.9671205674991441,95.571575988409293,17.070675193894829,48.536440789507168,16.852930829689988,5.4297123730344339,0.81445685595516504,23.049129023531172,401.45087097646882,8.5376538202011716,133.10919502280842,64.14022576530671]
[17.187194770116264,5.2386569659314377,32,0.5,64,4,4.296798692529066,15,21600,424.5,8.0164203290450254E-3,8.9044442965385846E-3,0.86002157126822087,3.2121805686868048,61.222500964554079,28.69955404384784,77.235994833355008,26.818053761581602,3.826060461106489,0.5739090691659734,16.241626657397049,408.25837334260297,6.8075023661341447,161.06212597759838,42.26631385134565]
[18.905914247127892,5.7625226625245816,32,0.5,64,4,4.7264785617819731,15,21600,424.5,4.9846183149354368E-3,5.4885529356921902E-3,0.53476228783200674,1.997337145052545,37.736542136609586,50.019805554640449,127.25580038799546,44.186041801387312,2.5941527785754652,0.38912291678631983,11.012178545052851,413.48782145494715,5.2294481123441869,194.88517243289425,26.833483774374209]
[20.796505671840684,6.338774928777041,32,0.5,64,4,5.1991264179601711,15,21600,424.5,2.968576767600593E-3,3.2424002801934456E-3,0.31847632126424869,1.1895090599219686,22.293121015848165,90.70354583440492,217.95934622240037,75.680328549444567,1.6857648954355204,0.25286473431532808,7.1560719811237847,417.34392801887623,3.8561065639290746,235.81105864380174,16.352526408669476]
[22.876156239024755,6.9726524216547459,32,0.5,64,4,5.7190390597561889,15,21600,424.5,1.6860424858621556E-3,1.8279022841892728E-3,0.18088284401235816,0.67559742238615772,12.567740965080834,171.80853522115103,389.7678814435514,135.33606994567756,1.0453844560696008,0.15680766841044014,4.4376570160154563,420.06234298398454,2.7184149651083089,285.33138095900063,9.5272204409192511]
[25.163771862927234,7.6699176638202218,32,0.5,64,4,6.2909429657318086,15,21600,424.5,9.0895979215975477E-4,9.7870239101957904E-4,9.7515474062722013E-2,0.36422029562426672,6.7290676523744057,341.42086017682504,731.1887416203765,253.88497972929738,0.6156960922329523,9.2354413834942847E-2,2.6136299115288826,421.8863700884711,1.8240271044865608,345.25097096039076,5.2831918167025922]
[27.68014904921996,8.4369094302022436,32,0.5,64,4,6.9200372623049899,15,21600,424.5,4.6272539678664432E-4,4.9509516855291368E-4,4.9642334917032474E-2,0.18541412091511628,3.4040265091061968,715.19776497015448,1446.3865065905311,502.21753701060112,0.34260770147733322,5.1391155221599982E-2,1.4543696927712795,423.04563030722875,1.1592602187576517,417.75367486207278,2.7749850893361923]
[30.448163954141958,9.2806003732224696,32,0.5,64,4,7.6120409885354894,15,21600,424.5,2.2116940759308988E-4,2.3527236696643813E-4,2.3727605792513377E-2,8.8622607635037459E-2,1.617615005928547,1587.505380921282,3033.8918875118134,1053.434683163824,0.17909029008182903,2.6863543512274352E-2,0.76023828139736416,423.73976171860261,0.69413141137385992,505.4819465831074,1.3732071265174972]
[33.492980349556156,10.208660410544717,32,0.5,64,4,8.3732450873890389,15,21600,424.5,9.8632892441580326E-5,1.0436464736988013E-4,1.0581582758203808E-2,3.9522211601891226E-2,0.71755906505604206,3755.2109402685987,6789.1028277804126,2357.3273707570875,8.738707708869381E-2,1.3108061563304073E-2,0.37095814224150525,424.12904185775852,0.38928013915591464,611.63315536556092,0.63646016528199767]
[36.842278384511772,11.229526451599188,32,0.5,64,4,9.210569596127943,15,21600,424.5,4.0757916879340819E-5,4.2916037620159999E-5,4.3726110005968171E-3,1.6331702087229113E-2,0.29506918872146143,9525.685565940772,16314.788393721185,5664.857081153189,3.9528115129052868E-2,5.9292172693579306E-3,0.16779684872282943,424.33220315127716,0.2031612935186331,740.07611799232791,0.27451405143266522]
[40.526506222962951,12.352479096759108,32,0.5,64,4,10.131626555740738,15,21600,424.5,1.5487931684147345E-5,1.6235029927775579E-5,1.6615839484407416E-3,6.2060160474261697E-3,0.11162393770032135,26089.883220045209,42404.67161376639,14723.844310335551,1.6448726034949668E-2,2.4673089052424501E-3,6.9824842018361338E-2,424.43017515798164,9.7972006704480918E-2,895.49210277071688,0.10940577410046219]
[44.579156845259249,13.587727006435019,32,0.5,64,4,11.144789211314812,15,21600,424.5,5.3670177928918001E-6,5.6028296405994273E-6,5.7578705778981614E-4,2.1505646608449632E-3,3.8522251546811534E-2,77735.13167891615,120139.80329268254,41715.209476625882,6.2442355331387344E-3,9.3663532997081023E-4,2.6506779838173931E-2,424.4734932201618,4.3318062180162542E-2,1083.5454443525678,3.9978076052034565E-2]
[49.037072529785178,14.946499707078523,32,0.5,64,4,12.259268132446294,15,21600,{"$f":"H173*28.3","v":424.5},1.6804820638216799E-6,{"$f":"BESSELK(G173,1)","v":1.7477251228309701E-6},1.8028630806440668E-4,6.7336936062055886E-4,{"$f":"(I173/(2*3.14159*O$104*D173))*(1/F173)*L173","v":1.2016482944352687E-2},{"$f":"(A173-A172)/((O172+O173)/2)*1440","v":254038.75464430766},374178.55793699017,129923.11039478824,2.1425830902597497E-3,3.2138746353896249E-4,9.0952652181526383E-3,424.49090473478185,1.7411514620050639E-2,1311.0899876666081,1.3280182736379912E-2]
[{"$f":"A173*1.1","v":53.940779782763698},16.441149677786377,{"$f":"$C$108","v":32},{"$f":"$D$108","v":0.5},64,{"$f":"$F$108","v":4},13.485194945690925,{"$f":"$H$108","v":15},21600,424.5,4.7065081553023674E-7,4.8779949982270859E-7,5.0492593611193895E-5,1.8858983713780921E-4,3.3538651435007453E-3,918826.09345319413,1293004.6513901842,{"$f":"Q174*500/1440","v":448959.94839936949},{"$f":"G174*BESSELK(G174,1)*100","v":6.578071349519751E-4},{"$f":"H173*S174/100","v":9.8671070242796271E-5},2.7923912878711345E-3,{"$f":"J174-U174","v":424.49720760871213},6.302873930280839E-3,1586.4188850765959,3.9730199820311157E-3]
[59.33485776104007,18.085264645565015,32,0.5,64,4,14.833714440260017,15,21600,424.5,1.1659783276350424E-7,1.2046579992342201E-7,1.2508906372638253E-5,4.6720765301803876E-5,8.2826252895696619E-4,3714603.1384322913,5007607.789822476,1738752.704799471,1.7869552758815389E-4,2.6804329138223085E-5,7.5856251461171333E-4,424.49924143748541,2.0338287732784011E-3,1919.5668509426778,1.0595248465973511E-3]
[65.268343537144077,19.893791110121516,32,0.5,64,4,16.317085884286019,15,21600,424.5,2.5239881212762558E-8,2.6002111275006226E-8,2.7077974218212158E-6,1.011362337050224E-5,1.7877749914538006E-4,16968976.960509486,21976584.750331961,7630758.5938652633,4.242786828470384E-5,6.364180242705576E-6,1.801063008685678E-4,424.49981989369911,5.7845621370233857E-4,2322.6758896406427,2.4904732351263852E-4]
[71.795177890858497,21.883170221133671,32,0.5,64,4,17.948794472714624,15,21600,424.5,4.7101543896321894E-9,4.8396307707870459E-9,5.0531711322701413E-7,1.8873594179028977E-6,3.327487821421643E-5,88644528.171552956,110621112.92188492,38410108.653432265,8.6865538028682146E-6,1.3029830704302322E-6,3.687442089317557E-5,424.49996312557909,1.4323187997433706E-4,2810.4378264651823,5.0964258531378518E-5]
[78.974695679944347,24.071487243247038,32,0.5,64,4,19.743673919986087,15,21600,424.5,7.4661033961832153E-10,7.652896146333983E-10,8.00982197848576E-8,2.9916685089644314E-7,5.2617482472510429E-6,536554782.58435678,647175895.50624168,224713852.60633391,1.510962860567363E-6,2.2664442908510444E-7,6.4140373431084562E-6,424.49999358596267,3.0460383584340889E-5,3400.6297700228661,8.9572772234291381E-6]
[86.872165247938781,26.478635967571741,32,0.5,64,4,21.718041311984695,15,21600,424.5,9.8896178165801665E-11,1.0114789435852807E-10,1.0609828707510747E-8,3.9627710222552642E-8,6.954422818204178E-7,3818026676.3046031,4465202571.8108444,1550417559.6565433,2.1967341482987762E-7,3.2951012224481643E-8,9.3251364595283056E-7,424.49999906748633,5.4815236580907367E-6,4114.7620217276672,1.3321605548865269E-6]
[95.559381772732664,29.126499564328917,32,0.5,64,4,23.889845443183166,15,21600,424.5,1.0752228909132438E-11,1.0975001430534369E-11,1.1535259406949355E-9,4.3084193884955837E-9,7.5458615191524797E-8,32454474613.250824,36919677185.061668,12819332355.924192,2.6219108791418024E-8,3.9328663187127039E-9,1.1130011681956953E-7,424.4999998886999,8.2121357536379946E-7,4978.8620462904764,1.6494001394869904E-7]
[105.11531995000594,32.039149520761811,32,0.5,64,4,26.278829987501485,15,21600,424.5,9.4075852165106647E-13,9.5849364515961832E-13,1.0092692109006483E-10,3.7696205027139211E-10,6.5901224333690134E-9,335423831581.25586,372343508766.3175,129285940543.86024,2.5188091545250184E-9,3.7782137317875273E-10,1.0692344860958703E-8,424.49999998930764,1.0060773547593271E-7,6024.4230760114842,1.6699978438855069E-8]
[115.62685194500655,35.243064472838,32,0.5,64,4,28.906712986251637,15,21600,424.5,6.4816872978915461E-14,6.5928614765735063E-14,6.9537158302501561E-12,2.5972128625984334E-11,4.5329214790595765E-10,4298087496664.4116,4670431005430.7295,1621677432441.2253,1.9057795446142551E-10,2.8586693169213826E-11,8.0900341668875127E-10,424.499999999191,9.8833652373286895E-9,7289.5519219739072,1.3558261664253863E-9]
[127.18953713950721,38.767370920121799,32,0.5,64,4,31.797384284876802,15,21600,424.5,3.4336379708073371E-15,3.4872176010798606E-15,3.6836924732110879E-13,1.3758591387443412E-12,2.397636234624028E-11,69773162580043.789,74443593585474.516,25848469994956.43,1.1088439814652254E-11,1.663265972197838E-12,4.7070427013198817E-11,424.49999999995293,7.6192918641027063E-10,8820.3578255884058,8.6383024529896816E-11]
[139.90849085345795,42.644108012133984,32,0.5,64,4,34.977122713364487,15,21600,424.5,1.3622789991703979E-16,1.3816170494266009E-16,1.4614868947519287E-14,5.4586535518984537E-14,9.4993071239768969E-13,1469556127339366,1543999720924840.5,536111014210014.06,4.8324989080670794E-13,7.2487483621006193E-14,2.0513957864744753E-12,424.49999999999795,4.5019987737759948E-11,10672.632968961989,4.2182644028597709E-12]
[153.89933993880376,46.908518813347392,32,0.5,64,4,38.474834984700941,15,21600,424.5,3.93251133071201E-18,3.9832912954851769E-18,4.2188962589888531E-16,1.5757577527323365E-15,2.7387116709207703E-14,4.1228804147180544E+16,4.2772803868105384E+16,1.4851668009758814E+16,1.5325647528978784E-14,2.2988471293468176E-15,6.5057373760514939E-14,424.49999999999994,1.9895196601282805E-12,12913.885892444006,1.5406049555481675E-13]
[169.28927393268415,51.599370694682129,32,0.5,64,4,42.322318483171038,15,21600,424.5,8.0012528006064862E-20,8.0952322105794208E-20,8.5839436097927107E-18,3.2061029382575773E-17,5.5658763794293817E-16,1.5861536950055457E+18,1.6289264988736512E+18,5.6559947877557338E+17,3.4260899581136695E-16,5.1391349371705044E-17,1.4543751872192527E-15,424.5,0,15625.801929857247,0]
[186.21820132595258,56.75930776415035,32,0.5,64,4,46.554550331488144,15,21600,424.5,1.1080025974968274E-21,1.1198397245256772E-21,1.1886928276651491E-19,4.4397677113293326E-19,7.6994572970230458E-18,8.6401605324467028E+19,8.8030531823340683E+19,3.0566156883104403E+19,5.2133634818630459E-18,7.8200452227945686E-19,2.2130727980508631E-17,424.5,0,18907.220335127276,0]
[204.84002145854785,62.435238540565386,32,0.5,64,4,51.210005364636963,15,21600,424.5,1.0048700547031408E-23,1.0146340276038512E-23,1.0780496629336914E-21,4.0265154910573374E-21,6.9761155963200767E-20,6.9029906040626726E+21,6.9910211358860132E+21,2.4274378944048655E+21,5.1959413996736425E-20,7.7939120995104641E-21,2.2056771241614616E-19,424.5,0,22877.736605503989,0]
[225.32402360440267,68.678762394621941,32,0.5,64,4,56.331005901100667,15,21600,424.5,5.7211839330711386E-26,5.7717426107322518E-26,6.1378288483788713E-24,2.2924790748695084E-23,3.9683612563006838E-22,8.4087249967710695E+23,8.4786352081299301E+23,2.943970558378448E+23,3.2512806706479266E-22,4.87692100597189E-23,1.3801686446900449E-21,424.5,0,27682.061292659899,0]
[247.85642596484297,75.546638634084147,32,0.5,64,4,61.964106491210742,15,21600,424.5,1.9518715180406604E-28,1.967558438997652E-28,2.0940164574167103E-26,7.8211514684514128E-26,1.3527946766557471E-24,1.6297118148862826E+26,1.6381904500944126E+26,5.6881612850500434E+25,1.2191800064173089E-24,1.8287700096259634E-25,5.1754191272414766E-24,424.5,0,33495.294164118444,0]
[272.64206856132728,83.101302497492554,32,0.5,64,4,68.16051714033182,15,21600,424.5,3.7911099199944711E-31,3.8188185155285781E-31,4.067197298064573E-29,1.5190981908271179E-28,2.6256284217678723E-27,5.2664587073448422E+28,5.2828406118457859E+28,1.8343196568908979E+28,2.6029264488350217E-27,3.9043896732525328E-28,1.1049422775304668E-26,424.5,0,40529.305938583275,0]
[299.90627541746005,91.411432747241832,32,0.5,64,4,74.976568854365013,15,21600,424.5,3.9624865066195597E-34,3.9888233585588625E-34,4.2510543754858747E-32,1.587768809243974E-31,2.7425152405269763E-30,2.9874366148270746E+31,2.9927194554389203E+31,1.0391386998051807E+31,2.9906828919088806E-30,4.486024337863321E-31,1.2695448876153199E-29,424.5,0,49040.460185685894,0]
[329.8969029592061,100.55257602196602,32,0.5,64,4,82.474225739801525,15,21600,424.5,2.0948138642514794E-37,2.1074751235935464E-37,2.2473685723795233E-35,8.3939216178375188E-35,1.4489943840418581E-33,3.1477453758805845E+34,3.1507380953360234E+34,1.0940062831027859E+34,1.7381237908427028E-33,2.607185686264054E-34,7.3783354921272738E-33,424.5,0,59338.956824679859,0]
[362.88659325512674,110.60783362416264,32,0.5,64,4,90.721648313781685,15,21600,424.5,5.2323662900360408E-41,5.2611239516380021E-41,5.6134130865163028E-39,2.096609787813839E-38,3.6172854304788611E-37,6.5553460069107452E+37,6.5584967450060816E+37,2.2772558142382226E+37,4.7729783687571619E-37,7.159467553135743E-38,2.0261293175374155E-36,424.5,0,71800.137757862685,0]
[399.17525258063944,121.66861698657891,32,0.5,64,4,99.793813145159859,15,21600,424.5,5.7288111286050812E-45,5.7574419276431174E-45,6.1460114940214715E-43,2.2955352930170195E-42,3.9585288225736442E-41,2.8889039877049942E+41,2.8895598373794947E+41,1.0033193879789911E+41,5.7455708392132616E-41,8.6183562588198924E-42,2.4389948212460297E-40,424.5,0,86878.166687013698,0]
[439.0927778387034,133.83547868523681,32,0.5,64,4,109.77319445967585,15,21600,424.5,2.5317855038896135E-49,2.5432908554961664E-49,2.7161626484082281E-47,1.0144867491804731E-46,1.7486394621423291E-45,2.9040433901302938E+45,2.9043323461140317E+45,1.0084487312895943E+45,2.7918516164789603E-45,4.1877774247184402E-46,1.1851410111953187E-44,424.5,0,105122.58169128676,0]
[{"$f":"A196*1.1","v":483.00205562257378},147.2190265537605,32,0.5,64,4,120.75051390564344,15,21600,424.5,4.1246383397528522E-54,4.1416816602478929E-54,4.4250149072335024E-52,1.6527430678517129E-51,2.847612955903046E-50,7.2317171974067806E+49,7.2320076306413923E+49,2.5111137606393723E+49,5.0011018890851163E-50,7.5016528336276742E-51,2.1229677519166318E-49,424.5,0,127198.32384645683,0]
[{"$f":"A197*1.1","v":531.3022611848312},161.94092920913656,32,0.5,64,4,132.8255652962078,15,21600,424.5,2.2418259563032007E-59,{"$f":"BESSELK(G198,1)","v":2.2502487793257611E-59},2.4050868122074133E-57,8.9829992435946885E-57,1.5471584017467729E-55,4.8849277762708846E+54,4.8850000963471913E+54,1.6961805890094413E+54,{"$f":"G198*BESSELK(G198,1)*100","v":2.9889056617104578E-55},4.4833584925656864E-56,1.2687904533960892E-54,424.5,0,153909.97185421293,0]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,"Effective Porosity, n = ",null,{"$f":"'Tab 2   Inputs and Plots'!R38","v":0.25}]
[{"$f":"'Tab 2   Inputs and Plots'!M38","v":"Best Fit"}]
["Radius, r",null,"Transmissivity, T","Thickness, b","Conductivity, K","Leakance, B","r/B","Flow Rate, Qw",null,null,"Ko(r/B)","K1(r/B)","Vacuum",null,"Velocity","Travel Time","Cummulative Travel Time","Time for 500 Pore Volumes","Q(r)/Qw","Qr","Qr","Qleak","Delta Q","Delta A","Qleak/A"]
["(ft)","(m)","(ft2/d)","(ft)","(ft/d)","B (ft)","(dim)","(ft3/min)","(ft3/day)","(L/min)","(dim)","(dim)","(ft-air)","(Pa)","(ft/day)","(min)","(min)","(days)","(%)","(scfm)","(L/min)","(L/min)","(L/min)","(ft2)","(L/min per 1000 ft2)"]
[0.1,{"$f":"A206*0.3048","v":3.0480000000000004E-2},{"$f":"'Tab 2   Inputs and Plots'!O38","v":86},{"$f":"'Tab 2   Inputs and Plots'!Q38","v":0.5},{"$f":"C206/D206","v":172},{"$f":"'Tab 2   Inputs and Plots'!P38","v":14},{"$f":"(A206/F206)","v":7.1428571428571435E-3},{"$f":"'Tab 2   Inputs and Plots'!$N$38","v":15},{"$f":"(H206*1440)","v":21600},{"$f":"H206*28.3","v":424.5},{"$f":"BESSELK(G206,0)","v":5.0576512083650176},{"$f":"BESSELK(G206,1)","v":139.98015137817811},{"$f":"(I206*K206/(2*3.1459*C206))","v":201.89672142605025},{"$f":"(M206*0.015)*249","v":754.08425452629763}]
[{"$f":"A206*1.1","v":0.11000000000000001},{"$f":"A207*0.3048","v":3.3528000000000009E-2},{"$f":"C206","v":86},{"$f":"$D$206","v":0.5},{"$f":"C207/D207","v":172},{"$f":"F206","v":14},{"$f":"(A207/F207)","v":7.8571428571428577E-3},{"$f":"$H$206","v":15},21600,{"$f":"H207*28.3","v":424.5},{"$f":"BESSELK(G207,0)","v":4.9623557833285874},{"$f":"BESSELK(G207,1)","v":127.25126819127453},{"$f":"(I207*K207/(2*3.1459*C207))","v":198.09261689429925},{"$f":"(M207*0.015)*249","v":739.87592410020773},{"$f":"(I207/(2*3.14159*O$202*D207))*(1/F207)*L207","v":249976.00331874989},{"$f":"(A207-A206)/((O206+O207)/2)*1440","v":1.1521105873221163E-4},{"$f":"P207","v":1.1521105873221163E-4},{"$f":"Q207*500/1440","v":4.0003839837573485E-5},{"$f":"G207*BESSELK(G207,1)*100","v":99.983139293144291},{"$f":"H207*S207/100","v":14.997470893971645},{"$f":"T207*28.3","v":424.42842629939759},{"$f":"J207-U207","v":7.1573700602414192E-2},null,{"$f":"(3.14159*A207*A207)-(3.14159*A206*A206)","v":6.5973390000000007E-3}]
[{"$f":"A207*1.1","v":0.12100000000000002},3.6880800000000012E-2,{"$f":"C207","v":86},{"$f":"$D$206","v":0.5},172,{"$f":"F207","v":14},8.6428571428571448E-3,{"$f":"$H$206","v":15},21600,424.5,4.8670631479138775,115.67928618572002,194.28862372164681,725.66800960035084,{"$f":"(I208/(2*3.14159*O$202*D208))*(1/F208)*L208","v":227243.67339118567},6.6384521733071412E-5,{"$f":"Q207+(P208)","v":1.8159558046528304E-4},{"$f":"Q208*500/1440","v":6.3054020994889946E-5},{"$f":"G208*BESSELK(G208,1)*100","v":99.979954489086609},{"$f":"H208*S208/100","v":14.996993173362991},424.41490680617267,{"$f":"J208-U208","v":8.509319382733338E-2},{"$f":"V208-V207","v":1.3519493224919188E-2},{"$f":"(3.14159*A208*A208)-(3.14159*A207*A207)","v":7.9827801900000106E-3},{"$f":"1000*W208/X208","v":1693.5820482511833}]
[0.13310000000000002,4.0568880000000009E-2,86,0.5,172,14,9.5071428571428581E-3,15,21600,424.5,4.7717738230830307,105.1590126696353,190.48476270441603,711.46058870099387,206577.34947354891,8.0328057340055671E-5,{"$f":"Q208+(P209)","v":2.6192363780533871E-4},9.0945707571298175E-5,99.976175616631863,14.996426342494779,424.39886549260223,0.10113450739777363,{"$f":"V209-V208","v":1.6041313570440252E-2},9.6591640299000039E-3,{"$f":"1000*W209/X209","v":1660.7351858591762}]
[0.14641000000000004,4.4625768000000017E-2,86,0.5,172,14,1.0457857142857145E-2,15,21600,424.5,4.6764884255827264,95.594816651094305,186.68105846255938,697.25375335765921,187789.17133077173,9.7200948807265168E-5,3.5912458661260387E-4,1.2469603701826523E-4,99.971693613476575,14.995754042021485,424.37983938920803,0.12016061079197016,1.9026103394196525E-2,1.1687588476179019E-2,1627.8895713152847]
[0.16105100000000006,4.9088344800000017E-2,86,0.5,172,14,1.1503642857142862E-2,15,21600,424.5,4.5812076852004378,86.899759536606197,182.87754012851249,683.04761237999412,170708.35432201019,1.1761888711287632E-4,4.7674347372548019E-4,1.6553592837690285E-4,99.96637980807121,14.994956971210682,424.35728228526233,0.14271771473767103,2.2557103945700874E-2,1.4141982056176602E-2,1595.0454367780019]
[0.17715610000000007,5.3997179280000022E-2,86,0.5,172,14,1.2654007142857148E-2,15,21600,424.5,4.4859324650447663,78.994804858444908,179.07424215676613,668.84229445552148,155179.63696657791,1.4232708550136825E-4,6.1907055922684842E-4,2.1495505528710014E-4,99.960082492736845,14.994012373910527,424.33055018166795,0.16944981833205475,2.6732103594383716E-2,1.7111798287973698E-2,1562.2030568915275]
[0.19487171000000009,5.9396897208000031E-2,86,0.5,172,14,1.3919407857142864E-2,15,21600,424.5,4.390663785359135,71.808099847212915,175.27120527448665,654.63795170020762,141061.86964469758,1.7222757669454179E-4,7.912981359213902E-4,2.7475629719492717E-4,99.952622921979469,14.992893438296919,424.29888430380282,0.20111569619717784,3.1665877865123093E-2,2.0705275928448161E-2,1529.3627563598675]
[0.21435888100000011,6.5336586928800039E-2,86,0.5,172,14,1.531134864285715E-2,15,21600,424.5,4.295402851458844,65.274322319226485,171.46847759673722,640.43476382381357,128226.73160454167,2.0841228414289825E-4,9.9971042006428848E-4,3.4712167363343347E-4,99.943790645590852,14.991568596838629,424.2613912905332,0.23860870946680279,3.7493013269624953E-2,2.5053383873422291E-2,1496.5249189112196]
[0.23579476910000013,7.187024562168004E-2,86,0.5,172,14,1.6842483507142868E-2,15,21600,424.5,4.2001510864735714,59.334086942147849,167.66611593352795,626.23294301172689,116557.5646135868,2.5220309750992927E-4,1.2519135175742178E-3,4.3469219360215897E-4,99.933338073450614,14.990000711017592,424.21702012179787,0.28297987820212711,4.4371168735324318E-2,3.0314594486840984E-2,1463.6899977199114]
[0.25937424601000014,7.9057270183848047E-2,86,0.5,172,14,1.8526731857857155E-2,15,21600,424.5,4.1049101696821984,53.93340548216225,163.86418732010634,612.03273964059713,105948.31265284728,3.0520044834359239E-4,1.5571139659178101E-3,5.4066457149923959E-4,99.920974154910297,14.988146123236545,424.16453528759422,0.33546471240578057,5.2484834203653463E-2,3.6680659329077575E-2,1430.858527726833]
[0.28531167061100016,8.6962997202232856E-2,86,0.5,172,14,2.0379405043642867E-2,15,21600,424.5,4.0096820813457787,49.023196126815797,160.06277080664759,597.83444896282879,96302.558016729585,3.6934220655553693E-4,1.926456172473347E-3,6.6890839321991221E-4,99.906357040232336,14.98595355603485,424.10248563578625,0.39751436421374819,6.2049651807967621E-2,4.4383597788183848E-2,1398.0311398839995]
[0.31384283767210019,9.5659296922456144E-2,86,0.5,172,14,2.2417345548007155E-2,15,21600,424.5,3.9144691550785704,44.558837423850214,156.26195954885745,583.63841891498248,87532.645057817834,4.4697511554763137E-4,2.3734312880209782E-3,8.2410808611839523E-4,99.889085574792318,14.983362836218848,424.02916826499342,0.47083173500658404,7.3317370792835845E-2,5.3704153323702486E-2,1365.2085780202965]
[0.34522712143931022,0.10522522661470177,86,0.5,172,14,2.4659080102807873E-2,15,21600,424.5,3.8192741389479141,40.499762782054226,152.46186324702242,569.4450592276288,79558.883612835838,5.4094147063387028E-4,2.9143727586548483E-3,1.0119349856440446E-3,99.868689458739226,14.980303418810884,423.94258675234801,0.55741324765199352,8.6581512645409475E-2,6.4982025521680087E-2,1332.391718330219]
[0.37974983358324127,0.11574774927617194,86,0.5,{"$f":"C220/D220","v":172},14,{"$f":"(A220/F220)","v":2.7124988113088663E-2},15,{"$f":"(H220*1440)","v":21600},424.5,3.7241002666621599,36.809091848980302,148.66261098776528,555.25485203930327,72308.824870570505,6.5468434315241555E-4,3.5690571018072636E-3,1.2392559381275219E-3,99.844617885717952,14.976692682857692,423.84040292487271,0.65959707512729437,0.10218382747530086,7.862825088123282E-2,1299.5815922402815]
[0.41772481694156544,0.12732252420378914,86,0.5,172,14,2.9837486924397531E-2,15,21600,424.5,3.6289513403929563,33.453295415706251,144.8643545502338,541.06836424512312,65716.603101273562,7.9237538820950925E-4,4.361432490016773E-3,1.5143862812558239E-3,99.81622645441432,14.972433968162147,423.71988129898875,0.78011870101124714,0.12052162588395277,9.5140183566291725E-2,1266.7794129278275]
[0.45949729863572203,0.14005477662416807,86,0.5,172,14,3.2821235616837287E-2,15,21600,424.5,3.5338318269843616,30.401890803695604,141.06727224667875,526.88626184134512,59722.337265963601,9.5907018129270515E-4,5.320502671309478E-3,1.8473967608713465E-3,99.782762126545208,14.967414318981783,423.57782522718446,0.92217477281553784,0.1420560718042907,0.11511962211521309,1233.9866062287738]
[0.50544702849929424,0.1540602542865849,86,0.5,172,14,3.6103359178521019E-2,15,21600,424.5,3.4387469695264476,27.627164966001782,137.27157337636817,512.70932656073512,54271.587068571607,1.1608971511387484E-3,6.4813998224482264E-3,2.2504860494611898E-3,99.743345985181477,14.96150189777722,423.41050370709536,1.0894962929046415,0.16732152008910361,0.13929474275940779,1201.2048464607465]
[0.55599173134922375,0.16946627971524342,86,0.5,172,14,3.9713695096373125E-2,15,21600,424.5,3.3437029165146046,25.103922787081856,133.47750338150627,498.53847512992587,49314.858508950485,1.4052875682355195E-3,7.8866873906837456E-3,2.7384331217651897E-3,99.696953528906235,14.954543029335934,423.21356773020693,1.2864322697930675,0.19693597688842601,0.16854663873888365,1168.4360979368078]
[0.61159090448414621,{"$f":"A225*0.3048","v":0.18641290768676777},86,0.5,172,14,4.3685064606010446E-2,15,21600,424.5,{"$f":"BESSELK(G225,0)","v":3.2487068710755564},22.809258294624406,{"$f":"(I225*K225/(2*3.1459*C225))","v":129.68534980419699},{"$f":"(M225*0.015)*249","v":484.37478151867572},44807.154444895481,1.7012557806970886E-3,{"$f":"Q224+(P225)","v":9.5879431713808347E-3},3.329146934507234E-3,99.642392221584686,14.946358833237703,422.98195498062699,1.5180450193730053,0.23161274957993783,0.2039414328740492,1135.6826629877507]
[0.67274999493256094,{"$f":"A226*0.3048","v":0.20505419845544459},86,0.5,172,14,4.8053571066611497E-2,15,21600,424.5,{"$f":"BESSELK(G226,0)","v":3.1537672630140516},20.722346705128512,{"$f":"(I226*K226/(2*3.1459*C226))","v":125.89544915438755},{"$f":"(M226*0.015)*249","v":470.21950259163748},40707.56608057666,2.0597410528748485E-3,{"$f":"Q225+(P226)","v":1.1647684224255684E-2},4.0443348000887792E-3,99.578276006185547,14.936741400927831,422.70978164625762,1.7902183537423753,0.27217333436936997,0.24676913377759946,1102.9472373747765]
[0.74002499442581704,{"$f":"A227*0.3048","v":0.22555961830098906},86,0.5,172,14,5.2858928173272646E-2,15,21600,424.5,{"$f":"BESSELK(G227,0)","v":3.0588939467149237},18.824255414383487,{"$f":"(I227*K227/(2*3.1459*C227))","v":122.10819480993412},{"$f":"(M227*0.015)*249","v":456.07410761510391},36978.901670872154,2.4940250747462283E-3,{"$f":"Q226+(P227)","v":1.4141709299001912E-2},4.9103157288201086E-3,99.502996486423541,14.92544947296353,422.39022008486791,2.1097799151320942,0.31956156138971892,0.29859065187089562,1070.2329740982336]
[0.81402749386839879,{"$f":"A228*0.3048","v":0.24811558013108798},86,0.5,172,14,5.8144820990599914E-2,15,21600,424.5,{"$f":"BESSELK(G228,0)","v":2.9640984282161078},17.097772216202817,{"$f":"(I228*K228/(2*3.1459*C228))","v":118.32404608114497},{"$f":"(M228*0.015)*249","v":441.94031211307646},33587.349069373049,3.0202426253189778E-3,{"$f":"Q227+(P228)","v":1.7161951924320889E-2},5.959011084833642E-3,99.414690484916562,14.912203572737486,422.01536110847087,2.48463889152913,0.3748589763970358,0.36129468876378312,1037.5435567006664]
[0.89543024325523879,{"$f":"A229*0.3048","v":0.27292713814419678},86,0.5,172,14,6.3959303089659914E-2,15,21600,424.5,{"$f":"BESSELK(G229,0)","v":2.8693941250383963},15.527249189313043,{"$f":"(I229*K229/(2*3.1459*C229))","v":114.54353858294213},{"$f":"(M229*0.015)*249","v":427.82011660728887},30502.169055356568,3.6580071920315795E-3,{"$f":"Q228+(P229)","v":2.0819959116352468E-2},7.229152470955718E-3,99.311203704794906,14.896680555719236,421.5760597268544,2.9239402731456039,0.43930138161647392,0.43716657340417875,1004.8832832658536]
[0.98497326758076276,{"$f":"A230*0.3048","v":0.3002198519586165},86,0.5,{"$f":"C230/D230","v":172},14,{"$f":"(A230/F230)","v":7.0355233398625913E-2},15,{"$f":"(H230*1440)","v":21600},424.5,{"$f":"BESSELK(G230,0)","v":2.7747966626022995},14.098460834596578,{"$f":"(I230*K230/(2*3.1459*C230))","v":110.76729606754614},{"$f":"(M230*0.015)*249","v":413.71585081228483},27695.416654559005,4.4311788351998832E-3,{"$f":"Q229+(P230)","v":2.5251137951552351E-2},8.7677562331779004E-3,99.190050257942858,14.878507538691428,421.0617633449674,3.4382366550325969,0.514296381886993,0.52897155381905536,972.2571623632482]
[1.0834705943388392,0.33024183715447819,86,0.5,172,14,7.7390756738488511E-2,15,21600,424.5,2.6803242112617021,12.798475174208068,106.99604387854542,399.63022388636716,25141.687922621011,5.3688085926225457E-3,3.0619946544174895E-2,1.063192588339406E-2,99.048367883072103,14.857255182460815,420.46032166364108,4.0396783363589179,0.60144168132632103,0.64005558012105812,939.67102233928847]
[1.1918176537727232,0.36326602086992604,86,0.5,172,14,8.5129832412337375E-2,15,21600,424.5,2.5859978681119182,11.615536641578894,103.23062419231792,385.56638135830741,22817.8898908882,6.5063027114823958E-3,3.7126249255657287E-2,1.2891058769325446E-2,98.882868767697531,14.83243031515463,419.75777791887606,4.7422220811239413,0.70254374476502335,0.77446725194648014,907.13163532649014]
[1.3109994191499956,0.39959262295691866,86,0.5,172,14,9.3642815653571118E-2,15,21600,424.5,2.4918420877531466,10.53895969802911,99.47201321370666,371.52796935319435,20703.031583863929,7.8868615979482658E-3,4.5013110853605556E-2,1.5629552379724149E-2,98.68978601829555,14.803467902744332,418.93814164766462,5.5618583523353777,0.81963627121143645,0.93710537485523915,874.64685744444807]
[1.4420993610649953,0.43955188525261057,86,0.5,172,14,0.10300709721892823,15,21600,424.5,2.3978851660668612,9.5590322085544805,95.721340487922248,357.51920672238958,18778.034207862605,9.5632634313109217E-3,5.4576374284916476E-2,1.8950129960040443E-2,98.46481600254377,14.769722400381566,417.98314393079835,6.5168560692016513,0.95499771686627355,1.1338975035748424,842.22578659486339]
[1.5863092971714949,0.48350707377787167,86,0.5,172,14,0.11330780694082107,15,21600,424.5,2.3041597807399494,8.6669276971823983,91.979910477762672,343.54496563444354,17025.558782940196,1.1600082039068182E-2,6.6176456323984653E-2,2.2977936223605781E-2,98.203057028239812,14.730458554235973,416.87197708487804,7.6280229151219601,1.1111668459203088,1.3720159793255577,809.87893921361274]
[1.7449402268886445,0.53185778115565885,86,0.5,172,14,0.12463858763490318,15,21600,424.5,2.2107035916849376,7.8546256818409192,88.249226531828896,329.61086109638092,15429.849646449624,1.4076454424517E-2,8.025291074850166E-2,2.7865594009896411E-2,97.898945138549053,14.684841770782358,415.5810221131407,8.9189778868592953,1.2909549717373352,1.660139334983926,777.61844715873485]
[1.919434249577509,0.58504355927122476,86,0.5,172,14,0.1371024463983935,15,21600,424.5,2.117559903576689,7.1148393606203353,84.531017332372215,315.72334973641023,13976.592397880349,1.7089547405508988E-2,9.7342458154010644E-2,3.3799464636809252E-2,97.546188207262986,14.631928231089448,414.08356893983142,10.416431060168577,1.4974531733092817,2.0087685953305474,745.45827567703111]
[2.1113776745352602,0.64354791519834731,86,0.5,172,14,0.15081269103823286,15,21600,424.5,2.0247783913643955,6.4409499862112094,80.82726585705673,301.88983797610683,12652.784982141629,2.0758918092206147E-2,0.11810137624621679,4.1007422307714161E-2,97.137700026318129,14.570655003947721,412.34953661172051,12.150463388279491,1.7340323281109136,2.4306100003499669,713.41446297894026]
[2.3225154419887866,0.70790270671818223,86,0.5,172,14,0.16589396014205618,15,21600,424.5,1.9324158877153086,5.8269473236875831,77.140240812978902,288.11879943647614,11446.620723141721,2.5232023465742409E-2,0.14333339971195919,4.9768541566652488E-2,96.665536706568872,14.499830505985331,410.34520331938489,14.154796680615107,2.0043332923356161,{"$f":"(3.14159*A239*A239)-(3.14159*A238*A238)","v":2.9410381004234623},681.50538139816149]
[2.5547669861876656,{"$f":"A240*0.3048","v":0.77869297739000054},86,0.5,{"$f":"C240/D240","v":172},14,{"$f":"(A240/F240)","v":0.18248335615626182},15,{"$f":"(H240*1440)","v":21600},424.5,{"$f":"BESSELK(G240,0)","v":1.8405372287819919},5.2673756391155981,{"$f":"(I240*K240/(2*3.1459*C240))","v":73.472530398907949},{"$f":"(M240*0.015)*249","v":274.41990103992117},10347.38222227752,3.0691215788486471E-2,{"$f":"Q239+(P240)","v":0.17402461550044565},6.0425213715432524E-2,96.120838476154887,14.418125771423233,{"$f":"T240*28.3","v":408.03295933127748},16.467040668722518,{"$f":"V240-V239","v":2.3122439881074115},{"$f":"(3.14159*A240*A240)-(3.14159*A239*A239)","v":3.5586561015123905},{"$f":"1000*W240/X240","v":649.75201934368783}]
[2.8102436848064323,0.85656227512900063,86,0.5,172,14,0.20073169177188802,15,21600,424.5,1.7492161513237989,4.7572847130937399,69.827078117538832,260.80413676900753,9345.3451280425143,3.7362670946139445E-2,0.21138728644658511,7.3398363349508722E-2,95.493780869984732,14.32406713049771,405.37109979308519,19.128900206914807,2.6618595381922887,4.3059738828299849,618.17828222470632]
[3.0912680532870755,0.94221850264190066,86,0.5,172,14,0.22080486094907684,15,21600,424.5,1.6585362299138531,4.292185414609877,66.207220187921266,247.28396740188592,8431.6908640504917,4.5527847363544802E-2,0.25691513381012993,8.9206643684072898E-2,94.77354036405896,14.216031054608843,402.31367884543027,22.186321154569725,3.0574209476549186,5.2102283982242881,586.81130921188151]
[3.4003948586157833,1.0364403529060908,86,0.5,172,14,0.24288534704398451,15,21600,424.5,1.5685918375822654,3.8680094068329067,62.61672389344146,233.87346374200382,7598.4274739488865,5.553827991626601E-2,0.31245341372639596,0.1084907686549986,93.948280714800731,14.092242107220109,398.81045163432907,25.68954836567093,3.5032272111012048,6.3043763618513857,555.68180102629901]
[3.7404343444773618,1.1400843881967,86,0.5,172,14,0.26717388174838297,15,21600,424.5,1.4794891066533642,3.4810725879211182,59.059825937548581,220.58844987674394,6838.3178035049732,6.7834799358187675E-2,0.3802882130845836,0.1320445184321471,93.005167596277431,13.950775139441614,394.80693644619771,29.69306355380229,4.0035151881313595,7.6282953978401835,524.82435188140244]
[4.1144777789250986,1.25409282701637,86,0.5,172,14,0.29389126992322134,15,21600,424.5,1.391346858627001,3.1280418969003096,55.541269563749672,207.44664182060504,6144.8142931306111,8.2972666625539176E-2,0.46326087971012275,0.16085447212157039,91.930420545307427,13.789563081796114,390.24463521483005,34.255364785169945,4.5623012313676554,9.2302374313866267,494.27777619825287]
[4.5259255568176089,1.3795021097180074,86,0.5,172,14,0.3232803969155435,15,21600,424.5,1.3042974626824302,2.8059051374399537,52.066338826284202,194.46777551617149,5511.9996988515832,0.10165467177785259,0.56491555148797534,0.196151233155547,90.709412653895086,13.606411898084264,385.06145671578469,39.438543284215314,5.1831784990453684,11.168587291977808,464.08541774735926]
[4.97851811249937,1.5174523206898081,86,0.5,172,14,0.35560843660709784,15,21600,424.5,1.2184875717860379,2.5119434912888625,48.640887974858408,181.67371658609616,4934.5330969203887,0.12477504123578921,0.68969059272376454,0.23947590025130713,89.326829778260759,13.399024466739114,379.19239240871696,45.307607591283045,5.8690643070677311,13.513990623293154,434.29542543500219]
[5.4763699237493073,1.669197552758789,86,0.5,172,14,0.39116928026780767,15,21600,424.5,1.1340786736291251,2.2437064086732756,45.271363447567964,169.08854247666633,4407.6005578015092,0.15347813137688426,0.8431687241006488,0.29276691809050304,87.76690210129928,13.165035315194892,372.57049942001544,51.929500579984563,6.6218929887015179,16.351928654184704,404.96097608687137]
[6.0240069161242387,1.836117308034668,86,0.5,172,14,0.43028620829458847,15,21600,424.5,1.0512473810604268,1.9989885757070467,41.964815464693466,156.73858576063009,3926.8699002981848,0.18923752216399495,1.0324062462646437,0.35847439106411239,86.013721466518504,12.902058219977775,365.12824762537105,59.371752374628954,7.4422517946443918,19.785833671563523,376.14042037260725]
[6.6264076077366632,2.0197290388381348,86,0.5,172,14,0.47331482912404738,15,21600,424.5,0.97018537390815351,1.7758086696163362,38.728895706290494,144.65242546299498,3488.4489577127565,0.23396350515251471,1.2663697514171584,0.43971171924206887,84.051657701645809,12.607748655246871,356.79928694348644,67.700713056513564,8.3289606818846096,23.940858742591885,347.89732362720167]
[7.28904836851033,2.2217019427219489,86,0.5,172,14,0.52064631203645217,15,21600,424.5,0.89109889202275439,1.5723896224058866,35.57183707492937,132.86081147486118,3088.8468072324754,0.29015045988950622,1.5565202113066645,0.54045840670370293,81.865885799001447,12.279882869850217,347.52068521676114,76.979314783238863,9.2786017267252987,28.968439078536136,320.30036901781784]
[8.0179532053613638,2.4438721369941439,86,0.5,172,14,0.57271094324009741,15,21600,424.5,0.81420766931691546,1.3871401238823893,32.502411143565546,121.39650562121732,2724.937433943559,0.36108081123188263,1.9176010225385471,0.66583368838143997,79.443032875486878,11.916454931323033,337.23567455644184,87.264325443558164,10.285010660319301,35.051811285028748,293.42308666120806]
[8.8197485258975004,2.6882593506935581,86,0.5,172,14,0.6299820375641072,15,21600,424.5,0.73974319228546193,1.2186371074691293,29.529858637277563,110.2940220102317,2393.9253254683317,0.45111006715276253,2.3687110896913097,0.82246912836503805,76.771948801463196,11.515792320219481,325.8969226622113,98.603077337788704,11.338751894230541,42.412691654884782,267.34336944457107]
[9.7017233784872516,2.9570852857629144,86,0.5,172,14,0.69298024132051794,15,21600,424.5,0.66794616619171809,1.0656089791583776,26.663788285788566,99.589249247420298,2093.3125264432483,0.5660692968117117,2.9347803865030215,1.0190209675357713,73.844596753048336,11.07668951295725,313.47031321669016,111.02968678330984,12.426609445521137,51.319356902410647,242.14273513114534]
[10.671895716335978,3.2527938143392063,86,0.5,172,14,0.76227826545256983,15,21600,424.5,0.59906308051622592,0.92691937378698164,23.914039719380927,89.318938351887766,1820.8667288855829,0.71383964574448167,3.6486200322475031,1.2668819556414941,70.657049246472255,10.598557386970837,299.93917405127468,124.56082594872532,13.531139165415482,62.096421851916887,217.90529569777107]
[11.739085287969576,3.5780731957731269,86,0.5,172,14,0.83850609199782689,15,21600,424.5,0.53334178546159383,0.80155125638477509,21.290506887093397,79.52004322329384,1574.5900404309505,0.90518188718492332,4.5538019194324262,1.581181222025148,67.210561152714604,10.08158417290719,285.30883209327351,139.19116790672649,14.630341958001168,75.136670440819387,194.71639975748732]
[12.912993816766535,3.9358805153504401,86,0.5,172,14,0.92235670119760971,15,21600,424.5,0.47102602653627673,0.68859123248220122,18.802919882400598,70.228905760766224,1352.6881630562457,1.1549488391324436,5.7087507585648698,1.982205124501691,63.512673766587945,9.5269010649881913,269.61130013916585,154.88869986083415,15.69753195410766,90.915371233391568,172.66092346265691]
[14.204293198443191,4.3294685668854846,86,0.5,172,14,1.0145923713173708,15,21600,424.5,0.41234893752306312,0.58721399250525519,16.460585188580932,61.480285679349784,1153.5398352075144,1.4838802462525911,7.1926310048174606,2.497441321117174,59.578283712664771,8.9367425568997163,252.90981436026198,171.59018563973802,16.701485778903873,110.00759919240375,151.8212005489994]
[15.624722518287511,4.7624154235740335,86,0.5,172,14,1.1160516084491079,15,21600,424.5,0.35752556569348182,0.49666689340920694,14.27208729224381,53.306246036530631,975.66654352358159,1.921296348731391,9.113927353548851,3.1645581088711285,55.430588525276704,8.314588278791506,235.30284828979961,189.19715171020039,17.606966070462363,133.10919502280842,132.27460407558914]
[17.187194770116264,5.2386569659314377,86,0.5,172,14,1.2276567692940188,15,21600,424.5,0.30674459755378625,0.41625477559988761,12.244958382822718,45.734919559842851,817.70269676524788,2.5091988778295753,11.623126231378427,4.0358077192286199,51.101799301616481,7.6652698952424725,216.92713803536196,207.57286196463804,18.375710254437649,161.06212597759838,114.09082143242955]
[18.905914247127892,5.7625226625245816,86,0.5,172,14,1.3504224462234209,15,21600,424.5,0.26015956663446665,0.34532522258095033,10.38532737572876,38.789197748346922,678.36666944795718,3.3086113555834129,14.931737586961839,5.1846311065839723,46.633493182041427,6.9950239773062144,197.95917855776588,226.54082144223412,18.967959477596082,194.88517243289425,97.328900094374347]
[20.796505671840684,6.338774928777041,86,0.5,172,14,1.4854646908457632,15,21600,424.5,0.21787995097683149,0.28325458882142024,8.6975645323140398,32.48540352819294,556.43335458820695,4.4095425957113301,19.34128018267317,6.715722285650406,42.076469021425481,6.3114703532138217,178.61461099595115,245.88538900404885,19.344567561814728,235.81105864380174,82.034183100102879]
[22.876156239024755,6.9726524216547459,86,0.5,172,14,1.6340111599303397,15,21600,424.5,0.17996269648754992,0.22943523789595288,7.1839430800870341,26.832027404125071,450.70909394402037,5.9469180771983634,25.288198259871535,8.7806243957887276,37.489973920325944,5.623496088048892,159.14493929178366,265.35506070821634,19.469671704167496,285.33138095900063,68.235297634384992]
[25.163771862927234,7.6699176638202218,86,0.5,172,14,1.7974122759233739,15,21600,424.5,0.14640481911446185,0.18326453297402295,5.844343898467284,21.828624460775305,360.01005061939935,8.1265294412000362,33.41472770107157,11.602336007316516,32.940192130887283,4.9410288196330923,139.83111559561652,284.66888440438345,19.313823696167105,345.25097096039076,55.941402981261717]
[27.68014904921996,8.4369094302022436,86,0.5,172,14,1.9771535035157115,15,21600,424.5,0.11713783496249713,0.14413618587707389,4.6760331742052186,17.464983905656492,283.14521490662793,11.268144233563413,44.682871934634981,15.514886088414924,28.497936489024845,4.2746904733537265,120.97374039591047,303.52625960408955,18.857375199706098,417.75367486207278,45.139938519827801]
[30.448163954141958,9.2806003732224696,86,0.5,172,14,2.1748688538672827,15,21600,424.5,9.2024763558566799E-2,0.11143456070374862,3.6735427745102016,13.720682262795602,218.90521416598148,15.878649762138565,60.561521696773546,21.028306144713039,24.235555531896587,3.6353333297844883,102.87993323290102,321.62006676709899,18.093807163009444,505.4819465831074,35.795160015738766]
[33.492980349556156,10.208660410544717,86,0.5,172,14,2.3923557392540111,15,21600,424.5,7.0860437472225382E-2,8.4532438180409578E-2,2.8286826068187461,10.565129536468017,166.05792105242858,22.778989509781841,83.340511206555391,28.937677502276173,20.223166363403774,3.0334749545105661,85.847341212649027,338.65265878735096,17.032592020251968,611.63315536556092,27.84772517780193]
[36.842278384511772,11.229526451599188,86,0.5,172,14,2.6315913131794124,15,21600,424.5,5.3375519125286673E-2,6.279276129331407E-2,2.1307009660898459,7.958168108345574,123.35188268502655,33.32982579063821,116.6703369971936,40.510533679581116,16.524488515003373,2.4786732772505058,70.146453746189309,354.35354625381069,15.700887466459733,740.07611799232791,21.21523325067287]
[40.526506222962951,12.352479096759108,86,0.5,172,14,2.8947504444973537,15,21600,424.5,3.9244722742560301E-2,4.5574125653319995E-2,1.5666127474137663,5.8512986115904164,89.527106075195945,49.843228946801688,166.51356594399527,57.817210397220585,13.192572049252632,1.9788858073878948,56.002468349077425,368.49753165092255,14.143985397111862,895.49210277071688,15.794651179334085]
[44.579156845259249,13.587727006435019,86,0.5,172,14,3.1842254889470891,15,21600,424.5,2.8098842798690935E-2,3.2239996987337767E-2,1.121679610396781,4.1894733448319768,63.333165228571318,76.354920036869572,242.86848598086485,84.329335410022523,10.265942017065829,1.5398913025598742,43.578923862444441,380.92107613755559,12.423544486633034,1083.5454443525678,11.465642305437648]
[49.037072529785178,14.946499707078523,86,0.5,172,14,3.5026480378417983,15,21600,{"$f":"H271*28.3","v":424.5},1.954009711347364E-2,{"$f":"BESSELK(G271,1)","v":2.2170778882981954E-2},0.78002246122311747,2.9133838926683437,43.552907365143149,{"$f":"(A271-A270)/((O270+O271)/2)*1440","v":120.11665186947542},362.98513785034027,126.03650619803481,7.7656435151901109,1.1648465272785167,32.965156721982019,391.534843278018,10.613767140462414,1311.0899876666081,8.0953765495167129]
[{"$f":"A271*1.1","v":53.940779782763698},16.441149677786377,{"$f":"C271","v":86},{"$f":"$D$206","v":0.5},172,{"$f":"F271","v":14},3.8529128416259786,{"$f":"$H$206","v":15},21600,424.5,1.3159662621111538E-2,1.4777585908437278E-2,0.52532146421663861,1.9620756688491452,{"$f":"(I272/(2*3.14159*O$202*D272))*(1/F272)*L272","v":29.029509226878766},194.57435494274338,557.55949279308368,{"$f":"Q272*500/1440","v":193.59704610870961},{"$f":"G272*BESSELK(G272,1)*100","v":5.6936750514849086},{"$f":"H272*S272/100","v":0.85405125772273638},24.169650593553442,{"$f":"J272-U272","v":400.33034940644654},8.7955061284285421,1586.4188850765959,5.544252032781289]
[59.33485776104007,18.085264645565015,86,0.5,172,14,4.2382041257885765,15,21600,424.5,8.5558918786267941E-3,9.5162185186001471E-3,0.34154322787492825,1.2756639561128569,18.693929780030693,325.52022445798133,883.07971725106495,306.62490182328645,4.0331676587436798,0.60497514881155201,17.120796711366921,407.37920328863311,7.0488538821865632,1919.5668509426778,3.6721064852338694]
[65.268343537144077,19.893791110121516,86,0.5,172,14,4.6620245383674339,15,21600,424.5,5.3514635540376169E-3,5.8996670926368365E-3,0.21362543636939868,0.79789100483970399,11.5894735014486,564.28397021118417,1447.3636874622491,502.55683592439203,2.7504392754071789,0.41256589131107679,11.675614724103474,412.82438527589653,5.4451819872634246,2322.6758896406427,2.3443572181333856]
[71.795177890858497,21.883170221133671,86,0.5,172,14,5.1282269922041781,15,21600,424.5,3.2077354264439546E-3,3.5075581726623463E-3,0.12804980792864654,0.47826603261349476,6.8903468379757369,1017.1788790931008,2464.5425665553498,855.74394672060748,1.7987554497773408,0.26981331746660109,7.6357168843048111,416.86428311569517,4.0398978397986411,2810.4378264651823,1.4374620928297879]
[78.974695679944347,24.071487243247038,86,0.5,172,14,5.6410496914245964,15,21600,424.5,1.8348796305952503E-3,1.9913232006883511E-3,7.3246684353383926E-2,0.27357636605988894,3.9118118200263821,1914.1554838439583,4378.6980503993082,1520.3812674997598,1.1233153126769662,0.16849729690154494,4.7684735023137224,419.73152649768627,2.8672433819911021,3400.6297700228661,0.84315070322160435]
[86.872165247938781,26.478635967571741,86,0.5,172,14,6.2051546605670556,15,21600,424.5,9.9696471586665863E-4,1.0744835835448125E-3,3.9797902073203849E-2,0.14864516424341637,2.1107460512095515,3776.5867663063832,8155.2848167056909,2831.696116911698,0.66673368161358848,0.10001005224203827,2.8302844784496832,421.6697155215503,1.9381890238640267,4114.7620217276672,0.47103307885840706]
[95.559381772732664,29.126499564328917,86,0.5,172,14,6.8256701266237618,15,21600,424.5,5.1190876734326829E-4,5.4819961051276369E-4,2.0434920783963539E-2,7.6324429128103818E-2,1.0768988757808895,7848.7987729009083,16004.083589606598,5556.9734686134025,0.37418297049037524,5.6127445573556284E-2,1.5884067097316428,422.91159329026834,1.2418777687180409,4978.8620462904764,0.24943004187941048]
[105.11531995000594,32.039149520761811,86,0.5,172,14,7.5082371392861385,15,21600,424.5,2.4700194365382858E-4,2.629639302124301E-4,9.8600873320584433E-3,3.6827426185238286E-2,0.51657380885734294,17271.147611039956,33275.231200646551,11553.899722446718,0.1974395547113616,2.9615933206704241E-2,0.83813090974973004,423.66186909025026,0.75027579998192095,6024.4230760114842,0.12453902896850445]
[115.62685194500655,35.243064472838,86,0.5,172,14,8.2590608532147538,15,21600,424.5,1.1130442493543022E-4,1.178597165083696E-4,4.4431688839096069E-3,1.659523578140238E-2,0.23152697260948241,40466.756479312979,73741.987679959537,25604.856833319282,9.7341057078526402E-2,1.460115856177896E-2,0.41321278729834454,424.08678721270167,0.42491812245140181,7289.5519219739072,5.8291391158146799E-2]
[127.18953713950721,38.767370920121799,86,0.5,172,14,9.0849669385362297,15,21600,424.5,4.6523058854179839E-5,4.9019707017052196E-5,1.8571571400247872E-3,6.9364819179925799E-3,9.6295703910470043E-2,101580.93306316811,175322.92074312764,60876.014146919319,4.4534241758665161E-2,6.6801362637997743E-3,0.18904785626553361,424.31095214373448,0.22416493103281709,8820.3578255884058,2.5414493999608576E-2]
[139.90849085345795,42.644108012133984,86,0.5,172,14,9.9934636323898527,15,21600,424.5,1.7902377794190038E-5,1.8777625857105222E-5,7.146462327017461E-4,2.6692036791410214E-3,3.688730124495402E-2,275039.49661918479,450362.41736231244,156375.83936191403,1.8765352110560438E-2,2.8148028165840655E-3,7.9658919709329049E-2,424.42034108029065,0.10938893655617221,10672.632968961989,1.0249479849470668E-2]
[153.89933993880376,46.908518813347392,86,0.5,172,14,10.992809995628841,15,21600,424.5,6.2900826357608422E-6,6.5701968734215965E-6,2.5109423511819774E-4,9.378369681664686E-4,1.2906681236108058E-2,809207.12419659633,1259569.5415589088,437350.53526350996,7.2224925863398279E-3,1.0833738879509741E-3,3.0659481029012569E-2,424.46934051897097,4.8999438680311869E-2,12913.885892444006,3.7943217934875619E-3]
[169.28927393268415,51.599370694682129,86,0.5,172,14,12.092090995191725,15,21600,424.5,1.999690623669107E-6,2.0807927119453955E-6,7.9825785557822231E-5,2.9814930905846604E-4,4.0875682675715662E-3,2608118.1103513059,3867687.6519102147,1342947.1013577136,2.5161134814975488E-3,3.774170222246323E-4,1.0680901728957094E-2,424.48931909827104,1.9978579300072852E-2,15625.801929857247,1.2785634548392981E-3]
[186.21820132595258,56.75930776415035,86,0.5,172,14,13.301300094710898,15,21600,424.5,5.6949901905970677E-7,5.905314441158375E-7,2.2733869946060587E-5,8.4911004248536297E-5,1.1600567313186808E-3,9290928.9255470242,13158616.577457238,4568964.0893948739,7.8548359535477526E-4,1.1782253930321629E-4,3.3343778622810208E-3,424.4966656221377,7.3465238666585719E-3,18907.220335127276,3.8855652689515866E-4]
[204.84002145854785,62.435238540565386,86,0.5,172,14,14.631430104181989,15,21600,424.5,1.4370620950703018E-7,1.4853835849785887E-7,5.7366179186195312E-6,2.1426267926043948E-5,2.9179296776052452E-4,36939665.322029017,50098281.899486259,17395236.77065495,2.1733286101513488E-4,3.2599929152270231E-5,9.2257799500924758E-4,424.49907742200497,2.4117998672750218E-3,22877.736605503989,1.0542126211448664E-4]
[225.32402360440267,68.678762394621941,86,0.5,172,14,16.094573114600191,15,21600,424.5,3.174399196608226E-8,3.2715710067473222E-8,1.2671905671009531E-6,4.7329567681220593E-6,6.4267669506516646E-5,165685054.75042763,215783336.64991391,74924769.670109004,5.2654538767700939E-5,7.8981808151551404E-6,2.2351851706889047E-4,424.49977648148291,6.9905947793813539E-4,27682.061292659899,2.5253158373848992E-5]
[247.85642596484297,75.546638634084147,86,0.5,172,14,17.704030426060211,15,21600,424.5,6.0572671893799522E-9,6.2260464442837391E-9,2.4180045953242753E-7,9.0312471635361673E-7,1.2230622364246745E-5,848297618.30106175,1064080954.9509757,369472553.80242211,1.1022611568366331E-5,1.6533917352549496E-6,4.6790986107715074E-5,424.49995320901388,1.7672753097031091E-4,33495.294164118444,5.2761898463823255E-6]
[272.64206856132728,83.101302497492554,86,0.5,172,14,19.474433468666234,15,21600,424.5,9.8394085791346639E-10,1.0088941783241094E-9,3.9278001804731579E-8,1.4670333674067244E-7,1.9819003618095809E-6,5022517962.064992,6086598917.0159674,2113402401.7416556,1.9647642552697553E-6,2.9471463829046328E-7,8.3404242636201105E-6,424.49999165957576,3.8450561874014966E-5,40529.305938583275,9.4871009960747002E-7]
[299.90627541746005,91.411432747241832,86,0.5,172,14,21.421876815532862,15,21600,424.5,1.3389076443515751E-10,1.3698094605256194E-10,5.3447945014430041E-9,1.9962807462889618E-8,2.6908925869069374E-7,34882842208.846519,40969441125.862488,14225500390.924473,2.9343889524131341E-7,4.4015834286197009E-8,1.2456481102993753E-6,424.49999875435191,7.0947761514617014E-6,49040.460185685894,1.4467189183376689E-7]
[329.8969029592061,100.55257602196602,86,0.5,172,14,23.56406449708615,15,21600,424.5,1.4994595836480069E-11,1.5309517522096042E-11,5.9857028762421939E-10,2.2356600242764595E-9,3.007445078786534E-8,288714856059.16693,329684297185.02942,114473714300.35744,3.607544583099417E-8,5.411316874649125E-9,1.5314026755257025E-7,424.49999984685974,1.0925078299806046E-6,59338.956824679859,1.841130832832936E-8]
[362.88659325512674,110.60783362416264,86,0.5,172,14,25.920470946794769,15,21600,424.5,1.3553939919250304E-12,1.3812958730021212E-12,5.4106064640762864E-11,2.0208615143324929E-10,2.7134568216227015E-9,2897724038503.6865,3227408335688.7158,1120627894336.3596,3.5803839545078994E-9,5.3705759317618498E-10,1.5198729886886035E-8,424.49999998480126,1.3794152664559078E-7,71800.137757862685,1.921187492853871E-9]
[399.17525258063944,121.66861698657891,86,0.5,172,14,28.512518041474245,15,21600,424.5,9.6792393027082796E-14,9.8475343663310587E-14,3.863862098443726E-12,1.4431524937687315E-11,1.9344776035860902E-10,35952793051859.617,39180201387548.336,13604236592898.729,2.8077800128405198E-10,4.2116700192607798E-11,1.1919026154508008E-9,424.49999999880811,1.4006843684910564E-8,86878.166687013698,1.6122397857877757E-10]
[439.0927778387034,133.83547868523681,86,0.5,172,14,31.363769845621672,15,21600,424.5,5.3337117168027871E-15,5.4180827312641308E-15,2.1291679957549063E-13,7.9524424641445748E-13,1.0643435511981898E-11,563289720817349.75,602469922204898.12,209190945210034.09,1.6993149978790546E-11,2.5489724968185818E-12,7.2135921659965871E-11,424.49999999992787,1.1197585081390571E-9,105122.58169128676,1.0651931203777408E-11]
[{"$f":"A294*1.1","v":483.00205562257378},147.2190265537605,86,0.5,172,14,34.500146830183844,15,21600,424.5,2.2099108687683562E-16,2.2417120888098476E-16,8.8217581771986156E-15,3.2949266791836824E-14,4.403682859252136E-13,1.1409325022644766E+16,1.2011794944849664E+16,4170762133628355.5,7.7339396214937868E-13,1.160090943224068E-13,3.2830573693241125E-12,424.4999999999967,6.8837380240438506E-11,127198.32384645683,5.4118150427464149E-13]
[{"$f":"A295*1.1","v":531.3022611848312},161.94092920913656,86,0.5,172,14,37.950161513202225,15,21600,424.5,6.691066224680076E-18,{"$f":"BESSELK(G296,1)","v":6.7786540406675925E-18},2.6710112618544779E-16,9.9762270630264753E-16,1.3316180412595442E-14,3.0661087681085696E+17,3.1862267175570662E+17,1.1063287213739813E+17,{"$f":"G296*BESSELK(G296,1)*100","v":2.5725101568545604E-14},3.8587652352818405E-15,1.0920305615847609E-13,424.49999999999989,3.1832314562052488E-12,153909.97185421293,2.0682425042741732E-14]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,"Effective Porosity, n = ",null,{"$f":"'Tab 2   Inputs and Plots'!R39","v":0.2}]
[{"$f":"'Tab 2   Inputs and Plots'!M39","v":"Best Fit (fast)"}]
["Radius, r",null,"Transmissivity, T","Thickness, b","Conductivity, K","Leakance, B","r/B","Flow Rate, Qw",null,null,"Ko(r/B)","K1(r/B)","Vacuum",null,"Velocity","Travel Time","Cummulative Travel Time","Time for 500 Pore Volumes","Q(r)/Qw","Qr","Qr","Qleak","Delta Q","Delta A","Qleak/A"]
["(ft)","(m)","(ft2/d)","(ft)","(ft/d)","B (ft)","(dim)","(ft3/min)","(ft3/day)","(L/min)","(dim)","(dim)","(ft-air)","(Pa)","(ft/day)","(min)","(min)","(days)","(%)","(scfm)","(L/min)","(L/min)","(L/min)","(ft2)","(L/min per 1000 ft2)"]
[0.1,{"$f":"A303*0.3048","v":3.0480000000000004E-2},{"$f":"'Tab 2   Inputs and Plots'!O39","v":86},{"$f":"'Tab 2   Inputs and Plots'!Q39","v":0.4},{"$f":"C303/D303","v":215},{"$f":"'Tab 2   Inputs and Plots'!P39","v":14},{"$f":"(A303/F303)","v":7.1428571428571435E-3},{"$f":"'Tab 2   Inputs and Plots'!N39","v":15},{"$f":"(H303*1440)","v":21600},{"$f":"H303*28.3","v":424.5},{"$f":"BESSELK(G303,0)","v":5.0576512083650176},{"$f":"BESSELK(G303,1)","v":139.98015137817811},{"$f":"(I303*K303/(2*3.1459*C303))","v":201.89672142605025},{"$f":"(M303*0.015)*249","v":754.08425452629763}]
[{"$f":"A303*1.1","v":0.11000000000000001},{"$f":"A304*0.3048","v":3.3528000000000009E-2},{"$f":"C303","v":86},{"$f":"$D$303","v":0.4},{"$f":"C304/D304","v":215},{"$f":"F303","v":14},{"$f":"(A304/F304)","v":7.8571428571428577E-3},{"$f":"$H$303","v":15},21600,{"$f":"H304*28.3","v":424.5},{"$f":"BESSELK(G304,0)","v":4.9623557833285874},127.25126819127453,{"$f":"(I304*K304/(2*3.1459*C304))","v":198.09261689429925},{"$f":"(M304*0.015)*249","v":739.87592410020773},{"$f":"(I304/(2*3.14159*O$299*D304))*(1/F304)*L304","v":390587.50518554659},{"$f":"(A304-A303)/((O303+O304)/2)*1440","v":7.3735077588615476E-5},{"$f":"P304","v":7.3735077588615476E-5},{"$f":"Q304*500/1440","v":2.5602457496047037E-5},{"$f":"G304*BESSELK(G304,1)*100","v":99.983139293144291},{"$f":"H304*S304/100","v":14.997470893971645},{"$f":"T304*28.3","v":424.42842629939759},{"$f":"J304-U304","v":7.1573700602414192E-2},null,{"$f":"(3.14159*A304*A304)-(3.14159*A303*A303)","v":6.5973390000000007E-3}]
[{"$f":"A304*1.1","v":0.12100000000000002},3.6880800000000012E-2,{"$f":"C304","v":86},{"$f":"$D$303","v":0.4},215,{"$f":"F304","v":14},8.6428571428571448E-3,{"$f":"$H$303","v":15},21600,424.5,4.8670631479138775,115.67928618572002,194.28862372164681,725.66800960035084,{"$f":"(I305/(2*3.14159*O$299*D305))*(1/F305)*L305","v":355068.23967372754},4.2486093909165708E-5,{"$f":"Q304+(P305)","v":1.1622117149778118E-4},{"$f":"Q305*500/1440","v":4.0354573436729579E-5},{"$f":"G305*BESSELK(G305,1)*100","v":99.979954489086609},{"$f":"H305*S305/100","v":14.996993173362991},424.41490680617267,{"$f":"J305-U305","v":8.509319382733338E-2},{"$f":"V305-V304","v":1.3519493224919188E-2},{"$f":"(3.14159*A305*A305)-(3.14159*A304*A304)","v":7.9827801900000106E-3},{"$f":"1000*W305/X305","v":1693.5820482511833}]
[0.13310000000000002,4.0568880000000009E-2,86,0.4,215,14,9.5071428571428581E-3,15,21600,424.5,4.7717738230830307,105.1590126696353,190.48476270441603,711.46058870099387,322777.10855242005,5.1409956697635638E-5,{"$f":"Q305+(P306)","v":1.6763112819541683E-4},5.8205252845630849E-5,99.976175616631863,14.996426342494779,424.39886549260223,0.10113450739777363,{"$f":"V306-V305","v":1.6041313570440252E-2},9.6591640299000039E-3,{"$f":"1000*W306/X306","v":1660.7351858591762}]
[0.14641000000000004,4.4625768000000017E-2,86,0.4,215,14,1.0457857142857145E-2,15,21600,424.5,4.6764884255827264,95.594816651094305,186.68105846255938,697.25375335765921,293420.58020433079,6.2208607236649728E-5,2.2983973543206656E-4,7.980546369168978E-5,99.971693613476575,14.995754042021485,424.37983938920803,0.12016061079197016,1.9026103394196525E-2,1.1687588476179019E-2,1627.8895713152847]
[0.16105100000000006,4.9088344800000017E-2,86,0.4,215,14,1.1503642857142862E-2,15,21600,424.5,4.5812076852004378,86.899759536606197,182.87754012851249,683.04761237999412,266731.80362814089,7.527608775224086E-5,3.051158231843074E-4,1.0594299416121785E-4,99.96637980807121,14.994956971210682,424.35728228526233,0.14271771473767103,2.2557103945700874E-2,1.4141982056176602E-2,1595.0454367780019]
[0.17715610000000007,5.3997179280000022E-2,86,0.4,215,14,1.2654007142857148E-2,15,21600,424.5,4.4859324650447663,78.994804858444908,179.07424215676613,668.84229445552148,242468.18276027791,9.1089334720875699E-5,3.9620515790518313E-4,1.3757123538374414E-4,99.960082492736845,14.994012373910527,424.33055018166795,0.16944981833205475,2.6732103594383716E-2,1.7111798287973698E-2,1562.2030568915275]
[0.19487171000000009,5.9396897208000031E-2,86,0.4,215,14,1.3919407857142864E-2,15,21600,424.5,4.390663785359135,71.808099847212915,175.27120527448665,654.63795170020762,220409.17131983989,1.102256490845068E-4,5.064308069896899E-4,1.7584403020475344E-4,99.952622921979469,14.992893438296919,424.29888430380282,0.20111569619717784,3.1665877865123093E-2,2.0705275928448161E-2,1529.3627563598675]
[0.21435888100000011,6.5336586928800039E-2,86,0.4,215,14,1.531134864285715E-2,15,21600,424.5,4.295402851458844,65.274322319226485,171.46847759673722,640.43476382381357,200354.2681320963,1.3338386185145492E-4,6.3981466884114485E-4,2.2215787112539749E-4,99.943790645590852,14.991568596838629,424.2613912905332,0.23860870946680279,3.7493013269624953E-2,2.5053383873422291E-2,1496.5249189112196]
[0.23579476910000013,7.187024562168004E-2,86,0.4,215,14,1.6842483507142868E-2,15,21600,424.5,4.2001510864735714,59.334086942147849,167.66611593352795,626.23294301172689,182121.19470872934,1.6140998240635475E-4,8.0122465124749962E-4,2.782030039053818E-4,99.933338073450614,14.990000711017592,424.21702012179787,0.28297987820212711,4.4371168735324318E-2,3.0314594486840984E-2,1463.6899977199114]
[0.25937424601000014,7.9057270183848047E-2,86,0.4,215,14,1.8526731857857155E-2,15,21600,424.5,4.1049101696821984,53.93340548216225,163.86418732010634,612.03273964059713,165544.23852007382,1.9532828693989918E-4,9.965529381873988E-4,3.4602532575951346E-4,99.920974154910297,14.988146123236545,424.16453528759422,0.33546471240578057,5.2484834203653463E-2,3.6680659329077575E-2,1430.858527726833]
[0.28531167061100016,8.6962997202232856E-2,86,0.4,215,14,2.0379405043642867E-2,15,21600,424.5,4.0096820813457787,49.023196126815797,160.06277080664759,597.83444896282879,150472.74690113994,2.363790121955437E-4,1.2329319503829425E-3,4.2810137166074397E-4,99.906357040232336,14.98595355603485,424.10248563578625,0.39751436421374819,6.2049651807967621E-2,4.4383597788183848E-2,1398.0311398839995]
[0.31384283767210019,9.5659296922456144E-2,86,0.4,215,14,2.2417345548007155E-2,15,21600,424.5,3.9144691550785704,44.558837423850214,156.26195954885745,583.63841891498248,136769.75790284033,2.8606407395048418E-4,1.5189960243334267E-3,5.2742917511577317E-4,99.889085574792318,14.983362836218848,424.02916826499342,0.47083173500658404,7.3317370792835845E-2,5.3704153323702486E-2,1365.2085780202965]
[0.34522712143931022,0.10522522661470177,86,0.4,215,14,2.4659080102807873E-2,15,21600,424.5,3.8192741389479141,40.499762782054226,152.46186324702242,569.4450592276288,124310.75564505598,3.4620254120567705E-4,1.8651985655391036E-3,6.4763839081218879E-4,99.868689458739226,14.980303418810884,423.94258675234801,0.55741324765199352,8.6581512645409475E-2,6.4982025521680087E-2,1332.391718330219]
[0.37974983358324127,0.11574774927617194,86,0.4,215,14,2.7124988113088663E-2,15,21600,424.5,3.7241002666621599,36.809091848980302,148.66261098776528,555.25485203930327,112982.53886026639,4.189979796175461E-4,2.2841965451566495E-3,7.9312380040161431E-4,99.844617885717952,14.976692682857692,423.84040292487271,0.65959707512729437,0.10218382747530086,7.862825088123282E-2,1299.5815922402815]
[0.41772481694156544,0.12732252420378914,86,0.4,215,14,2.9837486924397531E-2,15,21600,424.5,3.6289513403929563,33.453295415706251,144.8643545502338,541.06836424512312,102682.19234573992,5.0712024845408598E-4,2.7913167936107356E-3,9.6920722000372762E-4,99.81622645441432,14.972433968162147,423.71988129898875,0.78011870101124714,0.12052162588395277,9.5140183566291725E-2,1266.7794129278275]
[0.45949729863572203,0.14005477662416807,86,0.4,215,14,3.2821235616837287E-2,15,21600,424.5,3.5338318269843616,30.401890803695604,141.06727224667875,526.88626184134512,93316.151978068112,6.1380491602733148E-4,3.4051217096380672E-3,1.1823339269576621E-3,99.782762126545208,14.967414318981783,423.57782522718446,0.92217477281553784,0.1420560718042907,0.11511962211521309,1233.9866062287738]
[0.50544702849929424,0.1540602542865849,86,0.4,215,14,3.6103359178521019E-2,15,21600,424.5,3.4387469695264476,27.627164966001782,137.27157337636817,512.70932656073512,84799.354794643106,7.42974176728799E-4,4.1480958863668663E-3,1.4403110716551619E-3,99.743345985181477,14.96150189777722,423.41050370709536,1.0894962929046415,0.16732152008910361,0.13929474275940779,1201.2048464607465]
[0.55599173134922375,0.16946627971524342,86,0.4,215,14,3.9713695096373125E-2,15,21600,424.5,3.3437029165146046,25.103922787081856,133.47750338150627,498.53847512992587,77054.466420235112,8.9938404367073265E-4,5.0474799300375987E-3,1.7525971979297219E-3,99.696953528906235,14.954543029335934,423.21356773020693,1.2864322697930675,0.19693597688842601,0.16854663873888365,1168.4360979368078]
[0.61159090448414621,{"$f":"A322*0.3048","v":0.18641290768676777},86,0.4,215,14,4.3685064606010446E-2,15,21600,424.5,{"$f":"BESSELK(G322,0)","v":3.2487068710755564},22.809258294624406,{"$f":"(I322*K322/(2*3.1459*C322))","v":129.68534980419699},{"$f":"(M322*0.015)*249","v":484.37478151867572},70011.178820149173,1.088803699646137E-3,{"$f":"Q321+(P322)","v":6.1362836296837359E-3},2.1306540380846306E-3,99.642392221584686,14.946358833237703,422.98195498062699,1.5180450193730053,0.23161274957993783,0.2039414328740492,1135.6826629877507]
[0.67274999493256094,{"$f":"A323*0.3048","v":0.20505419845544459},86,0.4,215,14,4.8053571066611497E-2,15,21600,424.5,{"$f":"BESSELK(G323,0)","v":3.1537672630140516},20.722346705128512,{"$f":"(I323*K323/(2*3.1459*C323))","v":125.89544915438755},{"$f":"(M323*0.015)*249","v":470.21950259163748},63605.572000901011,1.3182342738399032E-3,{"$f":"Q322+(P323)","v":7.4545179035236386E-3},2.588374272056819E-3,99.578276006185547,14.936741400927831,422.70978164625762,1.7902183537423753,0.27217333436936997,0.24676913377759946,1102.9472373747765]
[0.74002499442581704,{"$f":"A324*0.3048","v":0.22555961830098906},86,0.4,215,14,5.2858928173272646E-2,15,21600,424.5,{"$f":"BESSELK(G324,0)","v":3.0588939467149237},18.824255414383487,{"$f":"(I324*K324/(2*3.1459*C324))","v":122.10819480993412},{"$f":"(M324*0.015)*249","v":456.07410761510391},57779.53386073772,1.5961760478375867E-3,{"$f":"Q323+(P324)","v":9.0506939513612245E-3},3.14260206644487E-3,99.502996486423541,14.92544947296353,422.39022008486791,2.1097799151320942,0.31956156138971892,0.29859065187089562,1070.2329740982336]
[0.81402749386839879,{"$f":"A325*0.3048","v":0.24811558013108798},86,0.4,215,14,5.8144820990599914E-2,15,21600,424.5,{"$f":"BESSELK(G325,0)","v":2.9640984282161078},17.097772216202817,{"$f":"(I325*K325/(2*3.1459*C325))","v":118.32404608114497},{"$f":"(M325*0.015)*249","v":441.94031211307646},52480.232920895374,1.9329552802041467E-3,{"$f":"Q324+(P325)","v":1.0983649231565371E-2},3.8137670942935318E-3,99.414690484916562,14.912203572737486,422.01536110847087,2.48463889152913,0.3748589763970358,0.36129468876378312,1037.5435567006664]
[0.89543024325523879,{"$f":"A326*0.3048","v":0.27292713814419678},86,0.4,215,14,6.3959303089659914E-2,15,21600,424.5,{"$f":"BESSELK(G326,0)","v":2.8693941250383963},15.527249189313043,{"$f":"(I326*K326/(2*3.1459*C326))","v":114.54353858294213},{"$f":"(M326*0.015)*249","v":427.82011660728887},47659.639148994625,2.3411246029002115E-3,{"$f":"Q325+(P326)","v":1.3324773834465582E-2},4.6266575814116603E-3,99.311203704794906,14.896680555719236,421.5760597268544,2.9239402731456039,0.43930138161647392,0.43716657340417875,1004.8832832658536]
[0.98497326758076276,{"$f":"A327*0.3048","v":0.3002198519586165},86,0.4,215,14,7.0355233398625913E-2,15,21600,424.5,{"$f":"BESSELK(G327,0)","v":2.7747966626022995},14.098460834596578,{"$f":"(I327*K327/(2*3.1459*C327))","v":110.76729606754614},{"$f":"(M327*0.015)*249","v":413.71585081228483},43274.08852274844,2.8359544545279256E-3,{"$f":"Q326+(P327)","v":1.6160728288993509E-2},5.6113639892338574E-3,99.190050257942858,14.878507538691428,421.0617633449674,3.4382366550325969,0.514296381886993,0.52897155381905536,972.2571623632482]
[1.0834705943388392,0.33024183715447819,86,0.4,215,14,7.7390756738488511E-2,15,21600,424.5,2.6803242112617021,12.798475174208068,106.99604387854542,399.63022388636716,39283.887379095322,3.4360374992784301E-3,1.9596765788271939E-2,6.8044325653722005E-3,99.048367883072103,14.857255182460815,420.46032166364108,4.0396783363589179,0.60144168132632103,0.64005558012105812,939.67102233928847]
[1.1918176537727232,0.36326602086992604,86,0.4,215,14,8.5129832412337375E-2,15,21600,424.5,2.5859978681119182,11.615536641578894,103.23062419231792,385.56638135830741,35652.952954512803,4.1640337353487343E-3,2.3760799523620674E-2,8.2502776123682883E-3,98.882868767697531,14.83243031515463,419.75777791887606,4.7422220811239413,0.70254374476502335,0.77446725194648014,907.13163532649014]
[1.3109994191499956,0.39959262295691866,86,0.4,215,14,9.3642815653571118E-2,15,21600,424.5,2.4918420877531466,10.53895969802911,99.47201321370666,371.52796935319435,32348.486849787383,5.0475914226868913E-3,2.8808390946307563E-2,1.000291352302346E-2,98.68978601829555,14.803467902744332,418.93814164766462,5.5618583523353777,0.81963627121143645,0.93710537485523915,874.64685744444807]
[1.4420993610649953,0.43955188525261057,86,0.4,215,14,0.10300709721892823,15,21600,424.5,2.3978851660668612,9.5590322085544805,95.721340487922248,357.51920672238958,29340.678449785315,6.1204885960389902E-3,3.4928879542346553E-2,1.2128083174425885E-2,98.46481600254377,14.769722400381566,417.98314393079835,6.5168560692016513,0.95499771686627355,1.1338975035748424,842.22578659486339]
[1.5863092971714949,0.48350707377787167,86,0.4,215,14,0.11330780694082107,15,21600,424.5,2.3041597807399494,8.6669276971823983,91.979910477762672,343.54496563444354,26602.435598344051,7.4240525050036383E-3,4.2352932047350189E-2,1.4705879183107704E-2,98.203057028239812,14.730458554235973,416.87197708487804,7.6280229151219601,1.1111668459203088,1.3720159793255577,809.87893921361274]
[1.7449402268886445,0.53185778115565885,86,0.4,215,14,0.12463858763490318,15,21600,424.5,2.2107035916849376,7.8546256818409192,88.249226531828896,329.61086109638092,24109.140072577531,9.0089308316908829E-3,5.136186287904107E-2,1.7833980166333703E-2,97.898945138549053,14.684841770782358,415.5810221131407,8.9189778868592953,1.2909549717373352,1.660139334983926,777.61844715873485]
[1.919434249577509,0.58504355927122476,86,0.4,215,14,0.1371024463983935,15,21600,424.5,2.117559903576689,7.1148393606203353,84.531017332372215,315.72334973641023,21838.425621688042,1.0937310339525753E-2,6.2299173218566824E-2,2.1631657367557924E-2,97.546188207262986,14.631928231089448,414.08356893983142,10.416431060168577,1.4974531733092817,2.0087685953305474,745.45827567703111]
[2.1113776745352602,0.64354791519834731,86,0.4,215,14,0.15081269103823286,15,21600,424.5,2.0247783913643955,6.4409499862112094,80.82726585705673,301.88983797610683,19769.976534596291,1.3285707579011938E-2,7.558488079757876E-2,2.6244750276937071E-2,97.137700026318129,14.570655003947721,412.34953661172051,12.150463388279491,1.7340323281109136,2.4306100003499669,713.41446297894026]
[2.3225154419887866,0.70790270671818223,86,0.4,215,14,0.16589396014205618,15,21600,424.5,1.9324158877153086,5.8269473236875831,77.140240812978902,288.11879943647614,17885.344879908935,1.6148495018075148E-2,9.1733375815653911E-2,3.1851866602657611E-2,96.665536706568872,14.499830505985331,410.34520331938489,14.154796680615107,2.0043332923356161,{"$f":"(3.14159*A336*A336)-(3.14159*A335*A335)","v":2.9410381004234623},681.50538139816149]
[2.5547669861876656,{"$f":"A337*0.3048","v":0.77869297739000054},86,0.4,{"$f":"C337/D337","v":215},14,{"$f":"(A337/F337)","v":0.18248335615626182},15,{"$f":"(H337*1440)","v":21600},424.5,{"$f":"BESSELK(G337,0)","v":1.8405372287819919},5.2673756391155981,{"$f":"(I337*K337/(2*3.1459*C337))","v":73.472530398907949},{"$f":"(M337*0.015)*249","v":274.41990103992117},16167.784722308623,1.9642378104631344E-2,{"$f":"Q336+(P337)","v":0.11137575392028526},3.8672136777876828E-2,96.120838476154887,14.418125771423233,{"$f":"T337*28.3","v":408.03295933127748},16.467040668722518,{"$f":"V337-V336","v":2.3122439881074115},{"$f":"(3.14159*A337*A337)-(3.14159*A336*A336)","v":3.5586561015123905},{"$f":"1000*W337/X337","v":649.75201934368783}]
[2.8102436848064323,0.85656227512900063,86,0.4,215,14,0.20073169177188802,15,21600,424.5,1.7492161513237989,4.7572847130937399,69.827078117538832,260.80413676900753,14602.101762566424,2.3912109405529253E-2,0.13528786332581452,4.6974952543685597E-2,95.493780869984732,14.32406713049771,405.37109979308519,19.128900206914807,2.6618595381922887,4.3059738828299849,618.17828222470632]
[3.0912680532870755,0.94221850264190066,86,0.4,215,14,0.22080486094907684,15,21600,424.5,1.6585362299138531,4.292185414609877,66.207220187921266,247.28396740188592,13174.51697507889,2.9137822312668676E-2,0.1644256856384832,5.7092251957806664E-2,94.77354036405896,14.216031054608843,402.31367884543027,22.186321154569725,3.0574209476549186,5.2102283982242881,586.81130921188151]
[3.4003948586157833,1.0364403529060908,86,0.4,215,14,0.24288534704398451,15,21600,424.5,1.5685918375822654,3.8680094068329067,62.61672389344146,233.87346374200382,11872.542928045134,3.5544499146410252E-2,0.19997018478489345,6.9434091939199125E-2,93.948280714800731,14.092242107220109,398.81045163432907,25.68954836567093,3.5032272111012048,6.3043763618513857,555.68180102629901]
[3.7404343444773618,1.1400843881967,86,0.4,215,14,0.26717388174838297,15,21600,424.5,1.4794891066533642,3.4810725879211182,59.059825937548581,220.58844987674394,10684.871567976517,4.3414271589240126E-2,0.24338445637413358,8.4508491796574159E-2,93.005167596277431,13.950775139441614,394.80693644619771,29.69306355380229,4.0035151881313595,7.6282953978401835,524.82435188140244]
[4.1144777789250986,1.25409282701637,86,0.4,215,14,0.29389126992322134,15,21600,424.5,1.391346858627001,3.1280418969003096,55.541269563749672,207.44664182060504,9601.2723330165791,5.310250664034509E-2,0.29648696301447869,0.1029468621578051,91.930420545307427,13.789563081796114,390.24463521483005,34.255364785169945,4.5623012313676554,9.2302374313866267,494.27777619825287]
[4.5259255568176089,1.3795021097180074,86,0.4,215,14,0.3232803969155435,15,21600,424.5,1.3042974626824302,2.8059051374399537,52.066338826284202,194.46777551617149,8612.4995294555956,6.5058989937825676E-2,0.36154595295230435,0.12553678921955011,90.709412653895086,13.606411898084264,385.06145671578469,39.438543284215314,5.1831784990453684,11.168587291977808,464.08541774735926]
[4.97851811249937,1.5174523206898081,86,0.4,215,14,0.35560843660709784,15,21600,424.5,1.2184875717860379,2.5119434912888625,48.640887974858408,181.67371658609616,7710.2079639381054,7.9856026390905124E-2,0.44140197934320946,0.15326457616083661,89.326829778260759,13.399024466739114,379.19239240871696,45.307607591283045,5.8690643070677311,13.513990623293154,434.29542543500219]
[5.4763699237493073,1.669197552758789,86,0.4,215,14,0.39116928026780767,15,21600,424.5,1.1340786736291251,2.2437064086732756,45.271363447567964,169.08854247666633,6886.8758715648573,9.8226004081205937E-2,0.53962798342441542,0.18737082757792203,87.76690210129928,13.165035315194892,372.57049942001544,51.929500579984563,6.6218929887015179,16.351928654184704,404.96097608687137]
[6.0240069161242387,1.836117308034668,86,0.4,215,14,0.43028620829458847,15,21600,424.5,1.0512473810604268,1.9989885757070467,41.964815464693466,156.73858576063009,6135.7342192159122,0.12111201418495682,0.66073999760937219,0.229423610281032,86.013721466518504,12.902058219977775,365.12824762537105,59.371752374628954,7.4422517946443918,19.785833671563523,376.14042037260725]
[6.6264076077366632,2.0197290388381348,86,0.4,215,14,0.47331482912404738,15,21600,424.5,0.97018537390815351,1.7758086696163362,38.728895706290494,144.65242546299498,5450.7014964261807,0.14973664329760947,0.81047664090698168,0.28141550031492418,84.051657701645809,12.607748655246871,356.79928694348644,67.700713056513564,8.3289606818846096,23.940858742591885,347.89732362720167]
[7.28904836851033,2.2217019427219489,86,0.4,215,14,0.52064631203645217,15,21600,424.5,0.89109889202275439,1.5723896224058866,35.57183707492937,132.86081147486118,4826.3231363007417,0.185696294329284,0.99617293523626571,0.34589338029037003,81.865885799001447,12.279882869850217,347.52068521676114,76.979314783238863,9.2786017267252987,28.968439078536136,320.30036901781784]
[8.0179532053613638,2.4438721369941439,86,0.4,215,14,0.57271094324009741,15,21600,424.5,0.81420766931691546,1.3871401238823893,32.502411143565546,121.39650562121732,4257.7147405368105,0.2310917191884049,1.2272646544246706,0.42613356056412177,79.443032875486878,11.916454931323033,337.23567455644184,87.264325443558164,10.285010660319301,35.051811285028748,293.42308666120806]
[8.8197485258975004,2.6882593506935581,86,0.4,215,14,0.6299820375641072,15,21600,424.5,0.73974319228546193,1.2186371074691293,29.529858637277563,110.2940220102317,3740.5083210442672,0.2887104429777681,1.5159750974024386,0.52638024215362456,76.771948801463196,11.515792320219481,325.8969226622113,98.603077337788704,11.338751894230541,42.412691654884782,267.34336944457107]
[9.7017233784872516,2.9570852857629144,86,0.4,215,14,0.69298024132051794,15,21600,424.5,0.66794616619171809,1.0656089791583776,26.663788285788566,99.589249247420298,3270.8008225675749,0.36228434995949554,1.8782594473619341,0.65217341922289374,73.844596753048336,11.07668951295725,313.47031321669016,111.02968678330984,12.426609445521137,51.319356902410647,242.14273513114534]
[10.671895716335978,3.2527938143392063,86,0.4,215,14,0.76227826545256983,15,21600,424.5,0.59906308051622592,0.92691937378698164,23.914039719380927,89.318938351887766,2845.1042638837225,0.45685737327646847,2.3351168206384028,0.81080445161055648,70.657049246472255,10.598557386970837,299.93917405127468,124.56082594872532,13.531139165415482,62.096421851916887,217.90529569777107]
[11.739085287969576,3.5780731957731269,86,0.4,215,14,0.83850609199782689,15,21600,424.5,0.53334178546159383,0.80155125638477509,21.290506887093397,79.52004322329384,2460.2969381733592,0.57931640779835114,2.9144332284367538,1.0119559820960951,67.210561152714604,10.08158417290719,285.30883209327351,139.19116790672649,14.630341958001168,75.136670440819387,194.71639975748732]
[12.912993816766535,3.9358805153504401,86,0.4,215,14,0.92235670119760971,15,21600,424.5,0.47102602653627673,0.68859123248220122,18.802919882400598,70.228905760766224,2113.5752547753832,0.73916725704476427,3.6536004854815181,1.2686112796810827,63.512673766587945,9.5269010649881913,269.61130013916585,154.88869986083415,15.69753195410766,90.915371233391568,172.66092346265691]
[14.204293198443191,4.3294685668854846,86,0.4,215,14,1.0145923713173708,15,21600,424.5,0.41234893752306312,0.58721399250525519,16.460585188580932,61.480285679349784,1802.4059925117408,0.94968335760165867,4.6032838430831768,1.5983624455149921,59.578283712664771,8.9367425568997163,252.90981436026198,171.59018563973802,16.701485778903873,110.00759919240375,151.8212005489994]
[15.624722518287511,4.7624154235740335,86,0.4,215,14,1.1160516084491079,15,21600,424.5,0.35752556569348182,0.49666689340920694,14.27208729224381,53.306246036530631,1524.4789742555959,1.2296296631880907,5.832913506271268,2.0253171896775237,55.430588525276704,8.314588278791506,235.30284828979961,189.19715171020039,17.606966070462363,133.10919502280842,132.27460407558914]
[17.187194770116264,5.2386569659314377,86,0.4,215,14,1.2276567692940188,15,21600,424.5,0.30674459755378625,0.41625477559988761,12.244958382822718,45.734919559842851,1277.6604636956995,1.6058872818109287,7.4388007880821965,2.5829169403063181,51.101799301616481,7.6652698952424725,216.92713803536196,207.57286196463804,18.375710254437649,161.06212597759838,114.09082143242955]
[18.905914247127892,5.7625226625245816,86,0.4,215,14,1.3504224462234209,15,21600,424.5,0.26015956663446665,0.34532522258095033,10.38532737572876,38.789197748346922,1059.947921012433,2.1175112675733843,9.5563120556555816,3.318163908213744,46.633493182041427,6.9950239773062144,197.95917855776588,226.54082144223412,18.967959477596082,194.88517243289425,97.328900094374347]
[20.796505671840684,6.338774928777041,86,0.4,215,14,1.4854646908457632,15,21600,424.5,0.21787995097683149,0.28325458882142024,8.6975645323140398,32.48540352819294,869.4271165440731,2.822107261255252,12.378419316910833,4.298062262816261,42.076469021425481,6.3114703532138217,178.61461099595115,245.88538900404885,19.344567561814728,235.81105864380174,82.034183100102879]
[22.876156239024755,6.9726524216547459,86,0.4,215,14,1.6340111599303397,15,21600,424.5,0.17996269648754992,0.22943523789595288,7.1839430800870341,26.832027404125071,704.23295928753168,3.8060275694069539,16.184446886317787,5.6195996133047865,37.489973920325944,5.623496088048892,159.14493929178366,265.35506070821634,19.469671704167496,285.33138095900063,68.235297634384992]
[25.163771862927234,7.6699176638202218,86,0.4,215,14,1.7974122759233739,15,21600,424.5,0.14640481911446185,0.18326453297402295,5.844343898467284,21.828624460775305,562.51570409281135,5.2009788423680243,21.38542572868581,7.425495044682572,32.940192130887283,4.9410288196330923,139.83111559561652,284.66888440438345,19.313823696167105,345.25097096039076,55.941402981261717]
[27.68014904921996,8.4369094302022436,86,0.4,215,14,1.9771535035157115,15,21600,424.5,0.11713783496249713,0.14413618587707389,4.6760331742052186,17.464983905656492,442.41439829160601,7.2116123094805857,28.597038038166396,9.929527096585554,28.497936489024845,4.2746904733537265,120.97374039591047,303.52625960408955,18.857375199706098,417.75367486207278,45.139938519827801]
[30.448163954141958,9.2806003732224696,86,0.4,215,14,2.1748688538672827,15,21600,424.5,9.2024763558566799E-2,0.11143456070374862,3.6735427745102016,13.720682262795602,342.03939713434602,10.162335847768684,38.759373885935076,13.458115932616346,24.235555531896587,3.6353333297844883,102.87993323290102,321.62006676709899,18.093807163009444,505.4819465831074,35.795160015738766]
[33.492980349556156,10.208660410544717,86,0.4,215,14,2.3923557392540111,15,21600,424.5,7.0860437472225382E-2,8.4532438180409578E-2,2.8286826068187461,10.565129536468017,259.46550164441959,14.57855328626038,53.337927172195457,18.520113601456757,20.223166363403774,3.0334749545105661,85.847341212649027,338.65265878735096,17.032592020251968,611.63315536556092,27.84772517780193]
[36.842278384511772,11.229526451599188,86,0.4,215,14,2.6315913131794124,15,21600,424.5,5.3375519125286673E-2,6.279276129331407E-2,2.1307009660898459,7.958168108345574,192.73731669535394,21.331088506008459,74.66901567820392,25.926741554931919,16.524488515003373,2.4786732772505058,70.146453746189309,354.35354625381069,15.700887466459733,740.07611799232791,21.21523325067287]
[40.526506222962951,12.352479096759108,86,0.4,215,14,2.8947504444973537,15,21600,424.5,3.9244722742560301E-2,4.5574125653319995E-2,1.5666127474137663,5.8512986115904164,139.88610324249365,31.899666525953091,106.56868220415701,37.003014654221182,13.192572049252632,1.9788858073878948,56.002468349077425,368.49753165092255,14.143985397111862,895.49210277071688,15.794651179334085]
[44.579156845259249,13.587727006435019,86,0.4,215,14,3.1842254889470891,15,21600,424.5,2.8098842798690935E-2,{"$f":"BESSELK(G367,1)","v":3.2239996987337767E-2},1.121679610396781,4.1894733448319768,98.958070669642666,48.86714882359653,155.43583102775355,53.970774662414435,10.265942017065829,1.5398913025598742,43.578923862444441,380.92107613755559,12.423544486633034,1083.5454443525678,11.465642305437648]
[49.037072529785178,14.946499707078523,86,0.4,215,14,3.5026480378417983,15,21600,{"$f":"H368*28.3","v":424.5},1.954009711347364E-2,2.2170778882981954E-2,0.78002246122311747,2.9133838926683437,68.051417758036152,{"$f":"(A368-A367)/((O367+O368)/2)*1440","v":76.87465719646427},232.31048822421781,80.663363966742295,7.7656435151901109,1.1648465272785167,32.965156721982019,391.534843278018,10.613767140462414,1311.0899876666081,8.0953765495167129]
[{"$f":"A368*1.1","v":53.940779782763698},16.441149677786377,{"$f":"C368","v":86},{"$f":"$D$303","v":0.4},215,{"$f":"F368","v":14},3.8529128416259786,{"$f":"$H$303","v":15},21600,424.5,1.3159662621111538E-2,1.4777585908437278E-2,0.52532146421663861,1.9620756688491452,{"$f":"(I369/(2*3.14159*O$299*D369))*(1/F369)*L369","v":45.35860816699806},124.5275871633558,356.83807538757361,{"$f":"Q369*500/1440","v":123.90210950957417},{"$f":"G369*BESSELK(G369,1)*100","v":5.6936750514849086},{"$f":"H369*S369/100","v":0.85405125772273638},24.169650593553442,{"$f":"J369-U369","v":400.33034940644654},8.7955061284285421,1586.4188850765959,5.544252032781289]
[59.33485776104007,18.085264645565015,86,0.4,215,14,4.2382041257885765,15,21600,424.5,8.5558918786267941E-3,9.5162185186001471E-3,0.34154322787492825,1.2756639561128569,29.209265281297952,208.33294365310809,565.1710190406817,196.23993716690336,4.0331676587436798,0.60497514881155201,17.120796711366921,407.37920328863311,7.0488538821865632,1919.5668509426778,3.6721064852338694]
[65.268343537144077,19.893791110121516,86,0.4,215,14,4.6620245383674339,15,21600,424.5,5.3514635540376169E-3,5.8996670926368365E-3,0.21362543636939868,0.79789100483970399,18.108552346013433,361.141740935158,926.31275997583975,321.63637499161104,2.7504392754071789,0.41256589131107679,11.675614724103474,412.82438527589653,5.4451819872634246,2322.6758896406427,2.3443572181333856]
[71.795177890858497,21.883170221133671,86,0.4,215,14,5.1282269922041781,15,21600,424.5,3.2077354264439546E-3,3.5075581726623463E-3,0.12804980792864654,0.47826603261349476,10.766166934337086,650.99448261958469,1577.3072425954244,547.67612590118904,1.7987554497773408,0.26981331746660109,7.6357168843048111,416.86428311569517,4.0398978397986411,2810.4378264651823,1.4374620928297879]
[78.974695679944347,24.071487243247038,86,0.4,215,14,5.6410496914245964,15,21600,424.5,1.8348796305952503E-3,1.9913232006883511E-3,7.3246684353383926E-2,0.27357636605988894,6.1122059687912209,1225.0595096601335,2802.3667522555579,973.04401119984652,1.1233153126769662,0.16849729690154494,4.7684735023137224,419.73152649768627,2.8672433819911021,3400.6297700228661,0.84315070322160435]
[86.872165247938781,26.478635967571741,86,0.4,215,14,6.2051546605670556,15,21600,424.5,9.9696471586665863E-4,1.0744835835448125E-3,3.9797902073203849E-2,0.14864516424341637,3.2980407050149232,2417.015530436086,5219.3822826916439,1812.2855148234873,0.66673368161358848,0.10001005224203827,2.8302844784496832,421.6697155215503,1.9381890238640267,4114.7620217276672,0.47103307885840706]
[95.559381772732664,29.126499564328917,86,0.4,215,14,6.8256701266237618,15,21600,424.5,5.1190876734326829E-4,5.4819961051276369E-4,2.0434920783963539E-2,7.6324429128103818E-2,1.6826544934076395,5023.2312146565828,10242.613497348226,3556.4630199125786,0.37418297049037524,5.6127445573556284E-2,1.5884067097316428,422.91159329026834,1.2418777687180409,4978.8620462904764,0.24943004187941048]
[105.11531995000594,32.039149520761811,86,0.4,215,14,7.5082371392861385,15,21600,424.5,2.4700194365382858E-4,2.629639302124301E-4,9.8600873320584433E-3,3.6827426185238286E-2,0.80714657633959819,11053.534471065575,21296.147968413803,7394.4958223659041,0.1974395547113616,2.9615933206704241E-2,0.83813090974973004,423.66186909025026,0.75027579998192095,6024.4230760114842,0.12453902896850445]
[115.62685194500655,35.243064472838,86,0.4,215,14,8.2590608532147538,15,21600,424.5,1.1130442493543022E-4,1.178597165083696E-4,4.4431688839096069E-3,1.659523578140238E-2,0.3617608947023162,25898.724146760309,47194.872115174112,16387.108373324347,9.7341057078526402E-2,1.460115856177896E-2,0.41321278729834454,424.08678721270167,0.42491812245140181,7289.5519219739072,5.8291391158146799E-2]
[127.18953713950721,38.767370920121799,86,0.4,215,14,9.0849669385362297,15,21600,424.5,4.6523058854179839E-5,4.9019707017052196E-5,1.8571571400247872E-3,6.9364819179925799E-3,0.15046203736010941,65011.797160427588,112206.6692756017,38960.64905402837,4.4534241758665161E-2,6.6801362637997743E-3,0.18904785626553361,424.31095214373448,0.22416493103281709,8820.3578255884058,2.5414493999608576E-2]
[139.90849085345795,42.644108012133984,86,0.4,215,14,9.9934636323898527,15,21600,424.5,1.7902377794190038E-5,1.8777625857105222E-5,7.146462327017461E-4,2.6692036791410214E-3,5.7636408195240636E-2,176025.27783627831,288231.94711188,100080.537191625,1.8765352110560438E-2,2.8148028165840655E-3,7.9658919709329049E-2,424.42034108029065,0.10938893655617221,10672.632968961989,1.0249479849470668E-2]
[153.89933993880376,46.908518813347392,86,0.4,215,14,10.992809995628841,15,21600,424.5,6.2900826357608422E-6,6.5701968734215965E-6,2.5109423511819774E-4,9.378369681664686E-4,2.0166689431418836E-2,517892.55948582187,806124.50659770193,279904.34256864648,7.2224925863398279E-3,1.0833738879509741E-3,3.0659481029012569E-2,424.46934051897097,4.8999438680311869E-2,12913.885892444006,3.7943217934875619E-3]
[169.28927393268415,51.599370694682129,86,0.4,215,14,12.092090995191725,15,21600,424.5,1.999690623669107E-6,2.0807927119453955E-6,7.9825785557822231E-5,2.9814930905846604E-4,6.3868254180805698E-3,1669195.5906248363,2475320.0972225382,859486.14486893686,2.5161134814975488E-3,3.774170222246323E-4,1.0680901728957094E-2,424.48931909827104,1.9978579300072852E-2,15625.801929857247,1.2785634548392981E-3]
[186.21820132595258,56.75930776415035,86,0.4,215,14,13.301300094710898,15,21600,424.5,5.6949901905970677E-7,5.905314441158375E-7,2.2733869946060587E-5,8.4911004248536297E-5,1.8125886426854385E-3,5946194.5123500954,8421514.6095726341,2924137.0172127201,7.8548359535477526E-4,1.1782253930321629E-4,3.3343778622810208E-3,424.4966656221377,7.3465238666585719E-3,18907.220335127276,3.8855652689515866E-4]
[204.84002145854785,62.435238540565386,86,0.4,215,14,14.631430104181989,15,21600,424.5,1.4370620950703018E-7,1.4853835849785887E-7,5.7366179186195312E-6,2.1426267926043948E-5,4.5592651212581945E-4,23641385.806098577,32062900.415671211,11132951.53321917,2.1733286101513488E-4,3.2599929152270231E-5,9.2257799500924758E-4,424.49907742200497,2.4117998672750218E-3,22877.736605503989,1.0542126211448664E-4]
[225.32402360440267,68.678762394621941,86,0.4,215,14,16.094573114600191,15,21600,424.5,3.174399196608226E-8,3.2715710067473222E-8,1.2671905671009531E-6,4.7329567681220593E-6,1.0041823360393223E-4,106038435.04027371,138101335.45594493,47951852.588869765,5.2654538767700939E-5,7.8981808151551404E-6,2.2351851706889047E-4,424.49977648148291,6.9905947793813539E-4,27682.061292659899,2.5253158373848992E-5]
[247.85642596484297,75.546638634084147,86,0.4,215,14,17.704030426060211,15,21600,424.5,6.0572671893799522E-9,6.2260464442837391E-9,2.4180045953242753E-7,9.0312471635361673E-7,1.9110347444135537E-5,542910475.71267974,681011811.16862464,236462434.43355021,1.1022611568366331E-5,1.6533917352549496E-6,4.6790986107715074E-5,424.49995320901388,1.7672753097031091E-4,33495.294164118444,5.2761898463823255E-6]
[272.64206856132728,83.101302497492554,86,0.4,215,14,19.474433468666234,15,21600,424.5,9.8394085791346639E-10,1.0088941783241094E-9,3.9278001804731579E-8,1.4670333674067244E-7,3.0967193153274691E-6,3214411495.7215958,3895423306.8902206,1352577537.11466,1.9647642552697553E-6,2.9471463829046328E-7,8.3404242636201105E-6,424.49999165957576,3.8450561874014966E-5,40529.305938583275,9.4871009960747002E-7]
[299.90627541746005,91.411432747241832,86,0.4,215,14,21.421876815532862,15,21600,424.5,1.3389076443515751E-10,1.3698094605256194E-10,5.3447945014430041E-9,1.9962807462889618E-8,4.2045196670420892E-7,22325019013.661781,26220442320.552002,9104320250.1916676,2.9343889524131341E-7,4.4015834286197009E-8,1.2456481102993753E-6,424.49999875435191,7.0947761514617014E-6,49040.460185685894,1.4467189183376689E-7]
[329.8969029592061,100.55257602196602,86,0.4,215,14,23.56406449708615,15,21600,424.5,1.4994595836480069E-11,1.5309517522096042E-11,5.9857028762421939E-10,2.2356600242764595E-9,4.6991329356039582E-8,184777507877.86685,210997950198.41885,73263177152.22876,3.607544583099417E-8,5.411316874649125E-9,1.5314026755257025E-7,424.49999984685974,1.0925078299806046E-6,59338.956824679859,1.841130832832936E-8]
[362.88659325512674,110.60783362416264,86,0.4,215,14,25.920470946794769,15,21600,424.5,1.3553939919250304E-12,1.3812958730021212E-12,5.4106064640762864E-11,2.0208615143324929E-10,4.2397762837854701E-9,1854543384642.3599,2065541334840.7788,717201852375.27039,3.5803839545078994E-9,5.3705759317618498E-10,1.5198729886886035E-8,424.49999998480126,1.3794152664559078E-7,71800.137757862685,1.921187492853871E-9]
[399.17525258063944,121.66861698657891,86,0.4,215,14,28.512518041474245,15,21600,424.5,9.6792393027082796E-14,9.8475343663310587E-14,3.863862098443726E-12,1.4431524937687315E-11,3.0226212556032652E-10,23009787553190.164,25075328888030.941,8706711419455.1875,2.8077800128405198E-10,4.2116700192607798E-11,1.1919026154508008E-9,424.49999999880811,1.4006843684910564E-8,86878.166687013698,1.6122397857877757E-10]
[439.0927778387034,133.83547868523681,86,0.4,215,14,31.363769845621672,15,21600,424.5,5.3337117168027871E-15,5.4180827312641308E-15,2.1291679957549063E-13,7.9524424641445748E-13,1.6630367987471711E-11,360505421323103.94,385580750211134.88,133882204934421.83,1.6993149978790546E-11,2.5489724968185818E-12,7.2135921659965871E-11,424.49999999992787,1.1197585081390571E-9,105122.58169128676,1.0651931203777408E-11]
[{"$f":"A391*1.1","v":483.00205562257378},147.2190265537605,86,0.4,215,14,34.500146830183844,15,21600,424.5,2.2099108687683562E-16,2.2417120888098476E-16,8.8217581771986156E-15,3.2949266791836824E-14,6.8807544675814603E-13,7301968014492652,7687548764703787,2669287765522148.5,7.7339396214937868E-13,1.160090943224068E-13,3.2830573693241125E-12,424.4999999999967,6.8837380240438506E-11,127198.32384645683,5.4118150427464149E-13]
[{"$f":"A392*1.1","v":531.3022611848312},161.94092920913656,86,0.4,215,14,37.950161513202225,15,21600,424.5,6.691066224680076E-18,6.7786540406675925E-18,2.6710112618544779E-16,9.9762270630264753E-16,2.0806531894680375E-14,1.9623096115894854E+17,2.0391850992365232E+17,7.0805038167934832E+16,{"$f":"G393*BESSELK(G393,1)*100","v":2.5725101568545604E-14},3.8587652352818405E-15,1.0920305615847609E-13,424.49999999999989,3.1832314562052488E-12,153909.97185421293,2.0682425042741732E-14]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,"Effective Porosity, n = ",null,{"$f":"'Tab 2   Inputs and Plots'!R40","v":0.3}]
[{"$f":"'Tab 2   Inputs and Plots'!M40","v":"Best Fit (slow)"}]
["Radius, r",null,"Transmissivity, T","Thickness, b","Conductivity, K","Leakance, B","r/B","Flow Rate, Qw",null,null,"Ko(r/B)","K1(r/B)","Vacuum",null,"Velocity","Travel Time","Cummulative Travel Time","Time for 500 Pore Volumes","Q(r)/Qw","Qr","Qr","Qleak","Delta Q","Delta A","Qleak/A"]
["(ft)","(m)","(ft2/d)","(ft)","(ft/d)","B (ft)","(dim)","(ft3/min)","(ft3/day)","(L/min)","(dim)","(dim)","(ft-air)","(Pa)","(ft/day)","(min)","(min)","(days)","(%)","(scfm)","(L/min)","(L/min)","(L/min)","(ft2)","(L/min per 1000 ft2)"]
[0.1,{"$f":"A400*0.3048","v":3.0480000000000004E-2},{"$f":"'Tab 2   Inputs and Plots'!O40","v":86},{"$f":"'Tab 2   Inputs and Plots'!Q40","v":0.6},{"$f":"C400/D400","v":143.33333333333334},{"$f":"'Tab 2   Inputs and Plots'!P40","v":14},{"$f":"(A400/F400)","v":7.1428571428571435E-3},{"$f":"'Tab 2   Inputs and Plots'!N40","v":15},{"$f":"(H400*1440)","v":21600},{"$f":"H400*28.3","v":424.5},{"$f":"BESSELK(G400,0)","v":5.0576512083650176},{"$f":"BESSELK(G400,1)","v":139.98015137817811},{"$f":"(I400*K400/(2*3.1459*C400))","v":201.89672142605025},{"$f":"(M400*0.015)*249","v":754.08425452629763}]
[{"$f":"A400*1.1","v":0.11000000000000001},{"$f":"A401*0.3048","v":3.3528000000000009E-2},{"$f":"C400","v":86},{"$f":"$D$400","v":0.6},{"$f":"C401/D401","v":143.33333333333334},{"$f":"F400","v":14},{"$f":"(A401/F401)","v":7.8571428571428577E-3},{"$f":"$H$400","v":15},21600,{"$f":"H401*28.3","v":424.5},{"$f":"BESSELK(G401,0)","v":4.9623557833285874},127.25126819127453,{"$f":"(I401*K401/(2*3.1459*C401))","v":198.09261689429925},{"$f":"(M401*0.015)*249","v":739.87592410020773},{"$f":"(I401/(2*3.14159*O$396*D401))*(1/F401)*L401","v":173594.44674913186},{"$f":"(A401-A400)/((O400+O401)/2)*1440","v":1.6590392457438476E-4},{"$f":"P401","v":1.6590392457438476E-4},{"$f":"Q401*500/1440","v":5.7605529366105823E-5},{"$f":"G401*BESSELK(G401,1)*100","v":99.983139293144291},{"$f":"H401*S401/100","v":14.997470893971645},{"$f":"T401*28.3","v":424.42842629939759},{"$f":"J401-U401","v":7.1573700602414192E-2},null,{"$f":"(3.14159*A401*A401)-(3.14159*A400*A400)","v":6.5973390000000007E-3}]
[{"$f":"A401*1.1","v":0.12100000000000002},3.6880800000000012E-2,{"$f":"C401","v":86},{"$f":"$D$400","v":0.6},143.33333333333334,{"$f":"F401","v":14},8.6428571428571448E-3,{"$f":"$H$400","v":15},21600,424.5,4.8670631479138775,115.67928618572002,194.28862372164681,725.66800960035084,{"$f":"(I402/(2*3.14159*O$396*D402))*(1/F402)*L402","v":157808.10652165674},9.5593711295622802E-5,{"$f":"Q401+(P402)","v":2.6149763587000755E-4},{"$f":"Q402*500/1440","v":9.0797790232641522E-5},{"$f":"G402*BESSELK(G402,1)*100","v":99.979954489086609},{"$f":"$T$6*S402/100","v":14.996993173362991},424.41490680617267,{"$f":"J402-U402","v":8.509319382733338E-2},{"$f":"V402-V401","v":1.3519493224919188E-2},{"$f":"(3.14159*A402*A402)-(3.14159*A401*A401)","v":7.9827801900000106E-3},{"$f":"1000*W402/X402","v":1693.5820482511833}]
[0.13310000000000002,4.0568880000000009E-2,86,0.6,143.33333333333334,14,9.5071428571428581E-3,15,21600,424.5,4.7717738230830307,105.1590126696353,190.48476270441603,711.46058870099387,143456.49268996451,1.1567240256968016E-4,{"$f":"Q402+(P403)","v":3.7717003843968771E-4},1.3096181890266936E-4,99.976175616631863,14.996426342494779,424.39886549260223,0.10113450739777363,{"$f":"V403-V402","v":1.6041313570440252E-2},9.6591640299000039E-3,{"$f":"1000*W403/X403","v":1660.7351858591762}]
[0.14641000000000004,4.4625768000000017E-2,86,0.6,143.33333333333334,14,1.0457857142857145E-2,15,21600,424.5,4.6764884255827264,95.594816651094305,186.68105846255938,697.25375335765921,130409.14675748038,1.3996936628246187E-4,5.1713940472214958E-4,1.7956229330630193E-4,99.971693613476575,14.995754042021485,424.37983938920803,0.12016061079197016,1.9026103394196525E-2,1.1687588476179019E-2,1627.8895713152847]
[0.16105100000000006,4.9088344800000017E-2,86,0.6,143.33333333333334,14,1.1503642857142862E-2,15,21600,424.5,4.5812076852004378,86.899759536606197,182.87754012851249,683.04761237999412,118547.46827917374,1.6937119744254192E-4,6.8651060216469147E-4,2.3837173686274009E-4,99.96637980807121,14.994956971210682,424.35728228526233,0.14271771473767103,2.2557103945700874E-2,1.4141982056176602E-2,1595.0454367780019]
[0.17715610000000007,5.3997179280000022E-2,86,0.6,143.33333333333334,14,1.2654007142857148E-2,15,21600,424.5,4.4859324650447663,78.994804858444908,179.07424215676613,668.84229445552148,107763.63678234577,2.049510031219703E-4,8.914616052866618E-4,3.0953527961342426E-4,99.960082492736845,14.994012373910527,424.33055018166795,0.16944981833205475,2.6732103594383716E-2,1.7111798287973698E-2,1562.2030568915275]
[0.19487171000000009,5.9396897208000031E-2,86,0.6,143.33333333333334,14,1.3919407857142864E-2,15,21600,424.5,4.390663785359135,71.808099847212915,175.27120527448665,654.63795170020762,97959.631697706645,2.4800771044014021E-4,1.1394693157268021E-3,3.9564906796069516E-4,99.952622921979469,14.992893438296919,424.29888430380282,0.20111569619717784,3.1665877865123093E-2,2.0705275928448161E-2,1529.3627563598675]
[0.21435888100000011,6.5336586928800039E-2,86,0.6,143.33333333333334,14,1.531134864285715E-2,15,21600,424.5,4.295402851458844,65.274322319226485,171.46847759673722,640.43476382381357,89046.341392042828,3.0011368916577351E-4,1.4395830048925756E-3,4.9985521003214435E-4,99.943790645590852,14.991568596838629,424.2613912905332,0.23860870946680279,3.7493013269624953E-2,2.5053383873422291E-2,1496.5249189112196]
[0.23579476910000013,7.187024562168004E-2,86,0.6,143.33333333333334,14,1.6842483507142868E-2,15,21600,424.5,4.2001510864735714,59.334086942147849,167.66611593352795,626.23294301172689,80942.753203879736,3.6317246041429809E-4,1.8027554653068738E-3,6.2595675878710899E-4,99.933338073450614,14.990000711017592,424.21702012179787,0.28297987820212711,4.4371168735324318E-2,3.0314594486840984E-2,1463.6899977199114]
[0.25937424601000014,7.9057270183848047E-2,86,0.6,143.33333333333334,14,1.8526731857857155E-2,15,21600,424.5,4.1049101696821984,53.93340548216225,163.86418732010634,612.03273964059713,73575.21712003283,4.3948864561477305E-4,2.2422441109216469E-3,7.7855698295890515E-4,99.920974154910297,14.988146123236545,424.16453528759422,0.33546471240578057,5.2484834203653463E-2,3.6680659329077575E-2,1430.858527726833]
[0.28531167061100016,8.6962997202232856E-2,86,0.6,143.33333333333334,14,2.0379405043642867E-2,15,21600,424.5,4.0096820813457787,49.023196126815797,160.06277080664759,597.83444896282879,66876.776400506657,5.3185277743997316E-4,2.7740968883616201E-3,9.6322808623667362E-4,99.906357040232336,14.98595355603485,424.10248563578625,0.39751436421374819,6.2049651807967621E-2,4.4383597788183848E-2,1398.0311398839995]
[0.31384283767210019,9.5659296922456144E-2,86,0.6,143.33333333333334,14,2.2417345548007155E-2,15,21600,424.5,3.9144691550785704,44.558837423850214,156.26195954885745,583.63841891498248,60786.559067929047,6.4364416638858918E-4,3.4177410547502093E-3,1.1867156440104893E-3,99.889085574792318,14.983362836218848,424.02916826499342,0.47083173500658404,7.3317370792835845E-2,5.3704153323702486E-2,1365.2085780202965]
[0.34522712143931022,0.10522522661470177,86,0.6,143.33333333333334,14,2.4659080102807873E-2,15,21600,424.5,3.8192741389479141,40.499762782054226,152.46186324702242,569.4450592276288,55249.224731136004,7.7895571771277323E-4,4.1966967724629822E-3,1.4571863793274241E-3,99.868689458739226,14.980303418810884,423.94258675234801,0.55741324765199352,8.6581512645409475E-2,6.4982025521680087E-2,1332.391718330219]
[0.37974983358324127,0.11574774927617194,86,0.6,143.33333333333334,14,2.7124988113088663E-2,15,21600,424.5,3.7241002666621599,36.809091848980302,148.66261098776528,555.25485203930327,50214.461715673962,9.4274545413947834E-4,5.1394422266024609E-3,1.7845285509036322E-3,99.844617885717952,14.976692682857692,423.84040292487271,0.65959707512729437,0.10218382747530086,7.862825088123282E-2,1299.5815922402815]
[0.41772481694156544,0.12732252420378914,86,0.6,143.33333333333334,14,2.9837486924397531E-2,15,21600,424.5,3.6289513403929563,33.453295415706251,144.8643545502338,541.06836424512312,45636.529931439974,1.1410205590216933E-3,6.2804627856241539E-3,2.1807162450083869E-3,99.81622645441432,14.972433968162147,423.71988129898875,0.78011870101124714,0.12052162588395277,9.5140183566291725E-2,1266.7794129278275]
[0.45949729863572203,0.14005477662416807,86,0.6,143.33333333333334,14,3.2821235616837287E-2,15,21600,424.5,3.5338318269843616,30.401890803695604,141.06727224667875,526.88626184134512,41473.84532358584,1.3810610610614958E-3,7.6615238466856495E-3,2.6602513356547394E-3,99.782762126545208,14.967414318981783,423.57782522718446,0.92217477281553784,0.1420560718042907,0.11511962211521309,1233.9866062287738]
[0.50544702849929424,0.1540602542865849,86,0.6,143.33333333333334,14,3.6103359178521019E-2,15,21600,424.5,3.4387469695264476,27.627164966001782,137.27157337636817,512.70932656073512,37688.602130952502,1.6716918976397977E-3,9.3332157443254474E-3,3.2406999112241136E-3,99.743345985181477,14.96150189777722,423.41050370709536,1.0894962929046415,0.16732152008910361,0.13929474275940779,1201.2048464607465]
[0.55599173134922375,0.16946627971524342,86,0.6,143.33333333333334,14,3.9713695096373125E-2,15,21600,424.5,3.3437029165146046,25.103922787081856,133.47750338150627,498.53847512992587,34246.429520104502,2.0236140982591477E-3,1.1356829842584595E-2,3.9433436953418737E-3,99.696953528906235,14.954543029335934,423.21356773020693,1.2864322697930675,0.19693597688842601,0.16854663873888365,1168.4360979368078]
[0.61159090448414621,{"$f":"A419*0.3048","v":0.18641290768676777},86,0.6,143.33333333333334,14,4.3685064606010446E-2,15,21600,424.5,{"$f":"BESSELK(G419,0)","v":3.2487068710755564},22.809258294624406,{"$f":"(I419*K419/(2*3.1459*C419))","v":129.68534980419699},{"$f":"(M419*0.015)*249","v":484.37478151867572},31116.079475621864,2.4498083242038074E-3,{"$f":"Q418+(P419)","v":1.3806638166788402E-2},4.7939715856904173E-3,99.642392221584686,14.946358833237703,422.98195498062699,1.5180450193730053,0.23161274957993783,0.2039414328740492,1135.6826629877507]
[0.67274999493256094,{"$f":"A420*0.3048","v":0.20505419845544459},86,0.6,143.33333333333334,14,4.8053571066611497E-2,15,21600,424.5,{"$f":"BESSELK(G420,0)","v":3.1537672630140516},20.722346705128512,{"$f":"(I420*K420/(2*3.1459*C420))","v":125.89544915438755},{"$f":"(M420*0.015)*249","v":470.21950259163748},28269.14311151157,2.9660271161397814E-3,{"$f":"Q419+(P420)","v":1.6772665282928183E-2},5.8238421121278418E-3,99.578276006185547,14.936741400927831,422.70978164625762,1.7902183537423753,0.27217333436936997,0.24676913377759946,1102.9472373747765]
[0.74002499442581704,{"$f":"A421*0.3048","v":0.22555961830098906},86,0.6,143.33333333333334,14,5.2858928173272646E-2,15,21600,424.5,{"$f":"BESSELK(G421,0)","v":3.0588939467149237},18.824255414383487,{"$f":"(I421*K421/(2*3.1459*C421))","v":122.10819480993412},{"$f":"(M421*0.015)*249","v":456.07410761510391},25679.792826994551,3.5913961076345685E-3,{"$f":"Q420+(P421)","v":2.0364061390562752E-2},7.0708546495009562E-3,99.502996486423541,14.92544947296353,422.39022008486791,2.1097799151320942,0.31956156138971892,0.29859065187089562,1070.2329740982336]
[0.81402749386839879,{"$f":"A422*0.3048","v":0.24811558013108798},86,0.6,143.33333333333334,14,5.8144820990599914E-2,15,21600,424.5,{"$f":"BESSELK(G422,0)","v":2.9640984282161078},17.097772216202817,{"$f":"(I422*K422/(2*3.1459*C422))","v":118.32404608114497},{"$f":"(M422*0.015)*249","v":441.94031211307646},23324.547964842397,4.3491493804593282E-3,{"$f":"Q421+(P422)","v":2.4713210771022079E-2},8.5809759621604444E-3,99.414690484916562,14.912203572737486,422.01536110847087,2.48463889152913,0.3748589763970358,0.36129468876378312,1037.5435567006664]
[0.89543024325523879,{"$f":"A423*0.3048","v":0.27292713814419678},86,0.6,143.33333333333334,14,6.3959303089659914E-2,15,21600,424.5,{"$f":"BESSELK(G423,0)","v":2.8693941250383963},15.527249189313043,{"$f":"(I423*K423/(2*3.1459*C423))","v":114.54353858294213},{"$f":"(M423*0.015)*249","v":427.82011660728887},21182.061843997617,5.2675303565254735E-3,{"$f":"Q422+(P423)","v":2.9980741127547554E-2},1.0409979558176234E-2,99.311203704794906,14.896680555719236,421.5760597268544,2.9239402731456039,0.43930138161647392,0.43716657340417875,1004.8832832658536]
[0.98497326758076276,{"$f":"A424*0.3048","v":0.3002198519586165},86,0.6,143.33333333333334,14,7.0355233398625913E-2,15,21600,424.5,{"$f":"BESSELK(G424,0)","v":2.7747966626022995},14.098460834596578,{"$f":"(I424*K424/(2*3.1459*C424))","v":110.76729606754614},{"$f":"(M424*0.015)*249","v":413.71585081228483},19232.928232332644,6.3808975226878322E-3,{"$f":"Q423+(P424)","v":3.6361638650235388E-2},1.2625568975776175E-2,99.190050257942858,14.878507538691428,421.0617633449674,3.4382366550325969,0.514296381886993,0.52897155381905536,972.2571623632482]
[1.0834705943388392,0.33024183715447819,86,0.6,143.33333333333334,14,7.7390756738488511E-2,15,21600,424.5,2.6803242112617021,12.798475174208068,106.99604387854542,399.63022388636716,17459.505501820146,7.7310843733764669E-3,4.4092723023611856E-2,1.5309973272087449E-2,99.048367883072103,14.857255182460815,420.46032166364108,4.0396783363589179,0.60144168132632103,0.64005558012105812,939.67102233928847]
[1.1918176537727232,0.36326602086992604,86,0.6,143.33333333333334,14,8.5129832412337375E-2,15,21600,424.5,2.5859978681119182,11.615536641578894,103.23062419231792,385.56638135830741,15845.756868672363,9.3690759045346513E-3,5.3461798928146509E-2,1.8563124627828647E-2,98.882868767697531,14.83243031515463,419.75777791887606,4.7422220811239413,0.70254374476502335,0.77446725194648014,907.13163532649014]
[1.3109994191499956,0.39959262295691866,86,0.6,143.33333333333334,14,9.3642815653571118E-2,15,21600,424.5,2.4918420877531466,10.53895969802911,99.47201321370666,371.52796935319435,14377.105266572175,1.1357080701045503E-2,6.4818879629192014E-2,2.2506555426802782E-2,98.68978601829555,14.803467902744332,418.93814164766462,5.5618583523353777,0.81963627121143645,0.93710537485523915,874.64685744444807]
[1.4420993610649953,0.43955188525261057,86,0.6,143.33333333333334,14,0.10300709721892823,15,21600,424.5,2.3978851660668612,9.5590322085544805,95.721340487922248,357.51920672238958,13040.301533237922,1.3771099341087726E-2,7.8589978970279736E-2,2.7288187142458238E-2,98.46481600254377,14.769722400381566,417.98314393079835,6.5168560692016513,0.95499771686627355,1.1338975035748424,842.22578659486339]
[1.5863092971714949,0.48350707377787167,86,0.6,143.33333333333334,14,0.11330780694082107,15,21600,424.5,2.3041597807399494,8.6669276971823983,91.979910477762672,343.54496563444354,11823.304710375136,1.6704118136258182E-2,9.5294097106537912E-2,3.3088228161992334E-2,98.203057028239812,14.730458554235973,416.87197708487804,7.6280229151219601,1.1111668459203088,1.3720159793255577,809.87893921361274]
[1.7449402268886445,0.53185778115565885,86,0.6,143.33333333333334,14,0.12463858763490318,15,21600,424.5,2.2107035916849376,7.8546256818409192,88.249226531828896,329.61086109638092,10715.173365590017,2.0270094371304476E-2,0.11556419147784239,4.012645537425083E-2,97.898945138549053,14.684841770782358,415.5810221131407,8.9189778868592953,1.2909549717373352,1.660139334983926,777.61844715873485]
[1.919434249577509,0.58504355927122476,86,0.6,143.33333333333334,14,0.1371024463983935,15,21600,424.5,2.117559903576689,7.1148393606203353,84.531017332372215,315.72334973641023,9705.9669429724654,2.460894826393294E-2,0.14017313974177534,4.8671229077005329E-2,97.546188207262986,14.631928231089448,414.08356893983142,10.416431060168577,1.4974531733092817,2.0087685953305474,745.45827567703111]
[2.1113776745352602,0.64354791519834731,86,0.6,143.33333333333334,14,0.15081269103823286,15,21600,424.5,2.0247783913643955,6.4409499862112094,80.82726585705673,301.88983797610683,8786.656237598354,2.9892842052776852E-2,0.17006598179455218,5.9050688123108395E-2,97.137700026318129,14.570655003947721,412.34953661172051,12.150463388279491,1.7340323281109136,2.4306100003499669,713.41446297894026]
[2.3225154419887866,0.70790270671818223,86,0.6,143.33333333333334,14,0.16589396014205618,15,21600,424.5,1.9324158877153086,5.8269473236875831,77.140240812978902,288.11879943647614,7949.0421688484175,3.6334113790669066E-2,0.20640009558522124,7.1666699855979593E-2,96.665536706568872,14.499830505985331,410.34520331938489,14.154796680615107,2.0043332923356161,{"$f":"(3.14159*A433*A433)-(3.14159*A432*A432)","v":2.9410381004234623},681.50538139816149]
[2.5547669861876656,{"$f":"A434*0.3048","v":0.77869297739000054},86,0.6,{"$f":"C434/D434","v":143.33333333333334},14,{"$f":"(A434/F434)","v":0.18248335615626182},15,{"$f":"(H434*1440)","v":21600},424.5,{"$f":"BESSELK(G434,0)","v":1.8405372287819919},5.2673756391155981,{"$f":"(I434*K434/(2*3.1459*C434))","v":73.472530398907949},{"$f":"(M434*0.015)*249","v":274.41990103992117},7185.6820988038344,4.4195350735420524E-2,{"$f":"Q433+(P434)","v":0.25059544632064179},8.7012307750222853E-2,96.120838476154887,{"$f":"$T$6*S434/100","v":14.418125771423233},{"$f":"T434*28.3","v":408.03295933127748},16.467040668722518,{"$f":"V434-V433","v":2.3122439881074115},{"$f":"(3.14159*A434*A434)-(3.14159*A433*A433)","v":3.5586561015123905},{"$f":"1000*W434/X434","v":649.75201934368783}]
[2.8102436848064323,0.85656227512900063,86,0.6,143.33333333333334,14,0.20073169177188802,15,21600,424.5,1.7492161513237989,4.7572847130937399,69.827078117538832,260.80413676900753,6489.82300558508,5.3802246162440795E-2,0.30439769248308257,0.10569364322329255,95.493780869984732,14.32406713049771,405.37109979308519,19.128900206914807,2.6618595381922887,4.3059738828299849,618.17828222470632]
[3.0912680532870755,0.94221850264190066,86,0.6,143.33333333333334,14,0.22080486094907684,15,21600,424.5,1.6585362299138531,4.292185414609877,66.207220187921266,247.28396740188592,5855.3408778128423,6.5560100203504501E-2,0.36995779268658707,0.12845756690506496,94.77354036405896,14.216031054608843,402.31367884543027,22.186321154569725,3.0574209476549186,5.2102283982242881,586.81130921188151]
[3.4003948586157833,1.0364403529060908,86,0.6,143.33333333333334,14,0.24288534704398451,15,21600,424.5,1.5685918375822654,3.8680094068329067,62.61672389344146,233.87346374200382,5276.6857457978385,7.9975123079423047E-2,0.44993291576601013,0.15622670686319795,93.948280714800731,14.092242107220109,398.81045163432907,25.68954836567093,3.5032272111012048,6.3043763618513857,555.68180102629901]
[3.7404343444773618,1.1400843881967,86,0.6,143.33333333333334,14,0.26717388174838297,15,21600,424.5,1.4794891066533642,3.4810725879211182,59.059825937548581,220.58844987674394,4748.8318079895644,9.7682111075790279E-2,0.54761502684180041,0.1901441065422918,93.005167596277431,13.950775139441614,394.80693644619771,29.69306355380229,4.0035151881313595,7.6282953978401835,524.82435188140244]
[4.1144777789250986,1.25409282701637,86,0.6,143.33333333333334,14,0.29389126992322134,15,21600,424.5,1.391346858627001,3.1280418969003096,55.541269563749672,207.44664182060504,4267.2321480073697,0.1194806399407764,0.66709566678257681,0.2316304398550614,91.930420545307427,13.789563081796114,390.24463521483005,34.255364785169945,4.5623012313676554,9.2302374313866267,494.27777619825287]
[4.5259255568176089,1.3795021097180074,86,0.6,143.33333333333334,14,0.3232803969155435,15,21600,424.5,1.3042974626824302,2.8059051374399537,52.066338826284202,194.46777551617149,3827.7775686469327,0.14638272736010774,0.81347839414268452,0.28245777574398773,90.709412653895086,13.606411898084264,385.06145671578469,39.438543284215314,5.1831784990453684,11.168587291977808,464.08541774735926]
[4.97851811249937,1.5174523206898081,86,0.6,143.33333333333334,14,0.35560843660709784,15,21600,424.5,1.2184875717860379,2.5119434912888625,48.640887974858408,181.67371658609616,3426.7590950836034,0.17967605937953646,0.99315445352222098,0.34484529636188227,89.326829778260759,13.399024466739114,379.19239240871696,45.307607591283045,5.8690643070677311,13.513990623293154,434.29542543500219]
[5.4763699237493073,1.669197552758789,86,0.6,143.33333333333334,14,0.39116928026780767,15,21600,424.5,1.1340786736291251,2.2437064086732756,45.271363447567964,169.08854247666633,3060.833720695493,0.22100850918271331,1.2141629627049344,0.42158436205032446,87.76690210129928,13.165035315194892,372.57049942001544,51.929500579984563,6.6218929887015179,16.351928654184704,404.96097608687137]
[6.0240069161242387,1.836117308034668,86,0.6,143.33333333333334,14,0.43028620829458847,15,21600,424.5,1.0512473810604268,1.9989885757070467,41.964815464693466,156.73858576063009,2726.9929863181842,0.27250203191615274,1.486664994621087,0.51620312313232186,86.013721466518504,12.902058219977775,365.12824762537105,59.371752374628954,7.4422517946443918,19.785833671563523,376.14042037260725]
[6.6264076077366632,2.0197290388381348,86,0.6,143.33333333333334,14,0.47331482912404738,15,21600,424.5,0.97018537390815351,1.7758086696163362,38.728895706290494,144.65242546299498,2422.5339984116363,0.3369074474196212,1.8235724420407082,0.63318487570857929,84.051657701645809,12.607748655246871,356.79928694348644,67.700713056513564,8.3289606818846096,23.940858742591885,347.89732362720167]
[7.28904836851033,2.2217019427219489,86,0.6,143.33333333333334,14,0.52064631203645217,15,21600,424.5,0.89109889202275439,1.5723896224058866,35.57183707492937,132.86081147486118,2145.0325050225524,0.41781666224088887,2.241389104281597,0.77826010565333237,81.865885799001447,12.279882869850217,347.52068521676114,76.979314783238863,9.2786017267252987,28.968439078536136,320.30036901781784]
[8.0179532053613638,2.4438721369941439,86,0.6,143.33333333333334,14,0.57271094324009741,15,21600,424.5,0.81420766931691546,1.3871401238823893,32.502411143565546,121.39650562121732,1892.317662460805,0.51995636817391089,2.761345472455508,0.95880051126927368,79.443032875486878,11.916454931323033,337.23567455644184,87.264325443558164,10.285010660319301,35.051811285028748,293.42308666120806]
[8.8197485258975004,2.6882593506935581,86,0.6,143.33333333333334,14,0.6299820375641072,15,21600,424.5,0.73974319228546193,1.2186371074691293,29.529858637277563,110.2940220102317,1662.4481426863415,0.64959849669997805,3.4109439691554861,1.1843555448456549,76.771948801463196,11.515792320219481,325.8969226622113,98.603077337788704,11.338751894230541,42.412691654884782,267.34336944457107]
[9.7017233784872516,2.9570852857629144,86,0.6,143.33333333333334,14,0.69298024132051794,15,21600,424.5,0.66794616619171809,1.0656089791583776,26.663788285788566,99.589249247420298,1453.6892544744783,0.81513978740886472,4.2260837565643508,1.4673901932515105,73.844596753048336,11.07668951295725,313.47031321669016,111.02968678330984,12.426609445521137,51.319356902410647,242.14273513114534]
[10.671895716335978,3.2527938143392063,86,0.6,143.33333333333334,14,0.76227826545256983,15,21600,424.5,0.59906308051622592,0.92691937378698164,23.914039719380927,89.318938351887766,1264.4907839483215,1.0279290898720537,5.2540128464364049,1.8243100161237518,70.657049246472255,10.598557386970837,299.93917405127468,124.56082594872532,13.531139165415482,62.096421851916887,217.90529569777107]
[11.739085287969576,3.5780731957731269,86,0.6,143.33333333333334,14,0.83850609199782689,15,21600,424.5,0.53334178546159383,0.80155125638477509,21.290506887093397,79.52004322329384,1093.4653058548267,1.3034619175462898,6.5574747639826949,2.2769009597162135,67.210561152714604,10.08158417290719,285.30883209327351,139.19116790672649,14.630341958001168,75.136670440819387,194.71639975748732]
[12.912993816766535,3.9358805153504401,86,0.6,143.33333333333334,14,0.92235670119760971,15,21600,424.5,0.47102602653627673,0.68859123248220122,18.802919882400598,70.228905760766224,939.36677990017063,1.6631263283507187,8.2206010923334141,2.8543753792824353,63.512673766587945,9.5269010649881913,269.61130013916585,154.88869986083415,15.69753195410766,90.915371233391568,172.66092346265691]
[14.204293198443191,4.3294685668854846,86,0.6,143.33333333333334,14,1.0145923713173708,15,21600,424.5,0.41234893752306312,0.58721399250525519,16.460585188580932,61.480285679349784,801.06933000521838,2.1367875546037314,10.357388646937146,3.5963155024087312,59.578283712664771,8.9367425568997163,252.90981436026198,171.59018563973802,16.701485778903873,110.00759919240375,151.8212005489994]
[15.624722518287511,4.7624154235740335,86,0.6,143.33333333333334,14,1.1160516084491079,15,21600,424.5,0.35752556569348182,0.49666689340920694,14.27208729224381,53.306246036530631,677.54621078026503,2.7666667421732032,13.12405538911035,4.5569636767744273,55.430588525276704,8.314588278791506,235.30284828979961,189.19715171020039,17.606966070462363,133.10919502280842,132.27460407558914]
[17.187194770116264,5.2386569659314377,86,0.6,143.33333333333334,14,1.2276567692940188,15,21600,424.5,0.30674459755378625,0.41625477559988761,12.244958382822718,45.734919559842851,567.84909497586659,3.6132463840745883,16.737301773184939,5.8115631156892151,51.101799301616481,7.6652698952424725,216.92713803536196,207.57286196463804,18.375710254437649,161.06212597759838,114.09082143242955]
[18.905914247127892,5.7625226625245816,86,0.6,143.33333333333334,14,1.3504224462234209,15,21600,424.5,0.26015956663446665,0.34532522258095033,10.38532737572876,38.789197748346922,471.08796489441477,4.7644003520401155,21.501702125225055,7.4658687934809222,46.633493182041427,6.9950239773062144,197.95917855776588,226.54082144223412,18.967959477596082,194.88517243289425,97.328900094374347]
[20.796505671840684,6.338774928777041,86,0.6,143.33333333333334,14,1.4854646908457632,15,21600,424.5,0.21787995097683149,0.28325458882142024,8.6975645323140398,32.48540352819294,386.41205179736596,6.349741337824315,27.851443463049371,9.6706400913365869,42.076469021425481,6.3114703532138217,178.61461099595115,245.88538900404885,19.344567561814728,235.81105864380174,82.034183100102879]
[22.876156239024755,6.9726524216547459,86,0.6,143.33333333333334,14,1.6340111599303397,15,21600,424.5,0.17996269648754992,0.22943523789595288,7.1839430800870341,26.832027404125071,312.99242635001417,8.5635620311656435,36.415005494215016,12.644099129935769,37.489973920325944,5.623496088048892,159.14493929178366,265.35506070821634,19.469671704167496,285.33138095900063,68.235297634384992]
[25.163771862927234,7.6699176638202218,86,0.6,143.33333333333334,14,1.7974122759233739,15,21600,424.5,0.14640481911446185,0.18326453297402295,5.844343898467284,21.828624460775305,250.00697959680514,11.702202395328053,48.117207889543067,16.707363850535788,32.940192130887283,4.9410288196330923,139.83111559561652,284.66888440438345,19.313823696167105,345.25097096039076,55.941402981261717]
[27.68014904921996,8.4369094302022436,86,0.6,143.33333333333334,14,1.9771535035157115,15,21600,424.5,0.11713783496249713,0.14413618587707389,4.6760331742052186,17.464983905656492,196.62862146293605,16.226127696331314,64.343335585874385,22.341435967317494,28.497936489024845,4.2746904733537265,120.97374039591047,303.52625960408955,18.857375199706098,417.75367486207278,45.139938519827801]
[30.448163954141958,9.2806003732224696,86,0.6,143.33333333333334,14,2.1748688538672827,15,21600,424.5,9.2024763558566799E-2,0.11143456070374862,3.6735427745102016,13.720682262795602,152.01750983748715,22.86525565747953,87.208591243353908,30.280760848386773,24.235555531896587,3.6353333297844883,102.87993323290102,321.62006676709899,18.093807163009444,505.4819465831074,35.795160015738766]
[33.492980349556156,10.208660410544717,86,0.6,143.33333333333334,14,2.3923557392540111,15,21600,424.5,7.0860437472225382E-2,8.4532438180409578E-2,2.8286826068187461,10.565129536468017,115.3180007308532,32.801744894085843,120.01033613743975,41.670255603277688,20.223166363403774,3.0334749545105661,85.847341212649027,338.65265878735096,17.032592020251968,611.63315536556092,27.84772517780193]
[36.842278384511772,11.229526451599188,86,0.6,143.33333333333334,14,2.6315913131794124,15,21600,424.5,5.3375519125286673E-2,6.279276129331407E-2,2.1307009660898459,7.958168108345574,85.66102964237956,47.994949138519011,168.00528527595876,58.335168498596794,16.524488515003373,2.4786732772505058,70.146453746189309,354.35354625381069,15.700887466459733,740.07611799232791,21.21523325067287]
[40.526506222962951,12.352479096759108,86,0.6,143.33333333333334,14,2.8947504444973537,15,21600,424.5,3.9244722742560301E-2,4.5574125653319995E-2,1.5666127474137663,5.8512986115904164,62.171601441108301,71.77424968339443,239.77953495935319,83.256782971997637,13.192572049252632,1.9788858073878948,56.002468349077425,368.49753165092255,14.143985397111862,895.49210277071688,15.794651179334085]
[44.579156845259249,13.587727006435019,86,0.6,143.33333333333334,14,3.1842254889470891,15,21600,424.5,2.8098842798690935E-2,{"$f":"BESSELK(G464,1)","v":3.2239996987337767E-2},1.121679610396781,4.1894733448319768,43.98136474206342,109.95108485309218,349.73061981244535,121.43424299043242,10.265942017065829,1.5398913025598742,43.578923862444441,380.92107613755559,12.423544486633034,1083.5454443525678,11.465642305437648]
[49.037072529785178,14.946499707078523,86,0.6,143.33333333333334,14,3.5026480378417983,15,21600,{"$f":"H465*28.3","v":424.5},1.954009711347364E-2,2.2170778882981954E-2,0.78002246122311747,2.9133838926683437,30.245074559127186,{"$f":"(A465-A464)/((O464+O465)/2)*1440","v":172.96797869204457},522.69859850448995,181.4925689251701,7.7656435151901109,1.1648465272785167,32.965156721982019,391.534843278018,10.613767140462414,1311.0899876666081,8.0953765495167129]
[{"$f":"A465*1.1","v":53.940779782763698},16.441149677786377,{"$f":"C465","v":86},{"$f":"$D$400","v":0.6},143.33333333333334,{"$f":"F465","v":14},3.8529128416259786,{"$f":"$H$400","v":15},21600,424.5,1.3159662621111538E-2,1.4777585908437278E-2,0.52532146421663861,1.9620756688491452,{"$f":"(I466/(2*3.14159*O$396*D466))*(1/F466)*L466","v":20.159381407554701},280.18707111755049,802.8856696220405,{"$f":"Q466*500/1440","v":278.77974639654184},{"$f":"G466*BESSELK(G466,1)*100","v":5.6936750514849086},0.85405125772273638,24.169650593553442,{"$f":"J466-U466","v":400.33034940644654},8.7955061284285421,1586.4188850765959,5.544252032781289]
[59.33485776104007,18.085264645565015,86,0.6,143.33333333333334,14,4.2382041257885765,15,21600,424.5,8.5558918786267941E-3,9.5162185186001471E-3,0.34154322787492825,1.2756639561128569,12.981895680576871,468.74912321949307,1271.6347928415335,441.53985862553242,4.0331676587436798,0.60497514881155201,17.120796711366921,407.37920328863311,7.0488538821865632,1919.5668509426778,3.6721064852338694]
[65.268343537144077,19.893791110121516,86,0.6,143.33333333333334,14,4.6620245383674339,15,21600,424.5,5.3514635540376169E-3,5.8996670926368365E-3,0.21362543636939868,0.79789100483970399,8.0482454871170841,812.56891710410514,2084.2037099456384,723.68184373112445,2.7504392754071789,0.41256589131107679,11.675614724103474,412.82438527589653,5.4451819872634246,2322.6758896406427,2.3443572181333856]
[71.795177890858497,21.883170221133671,86,0.6,143.33333333333334,14,5.1282269922041781,15,21600,424.5,3.2077354264439546E-3,3.5075581726623463E-3,0.12804980792864654,0.47826603261349476,4.7849630819275957,1464.737585894065,3548.9412958397033,1232.2712832776747,1.7987554497773408,0.26981331746660109,7.6357168843048111,416.86428311569517,4.0398978397986411,2810.4378264651823,1.4374620928297879]
[78.974695679944347,24.071487243247038,86,0.6,143.33333333333334,14,5.6410496914245964,15,21600,424.5,1.8348796305952503E-3,1.9913232006883511E-3,7.3246684353383926E-2,0.27357636605988894,2.7165359861294323,2756.3838967352995,6305.3251925750028,2189.3490251996536,1.1233153126769662,0.16849729690154494,4.7684735023137224,419.73152649768627,2.8672433819911021,3400.6297700228661,0.84315070322160435]
[86.872165247938781,26.478635967571741,86,0.6,143.33333333333334,14,6.2051546605670556,15,21600,424.5,9.9696471586665863E-4,1.0744835835448125E-3,3.9797902073203849E-2,0.14864516424341637,1.4657958688955219,5438.2849434811915,11743.610136056195,4077.6424083528459,0.66673368161358848,0.10001005224203827,2.8302844784496832,421.6697155215503,1.9381890238640267,4114.7620217276672,0.47103307885840706]
[95.559381772732664,29.126499564328917,86,0.6,143.33333333333334,14,6.8256701266237618,15,21600,424.5,5.1190876734326829E-4,5.4819961051276369E-4,2.0434920783963539E-2,7.6324429128103818E-2,0.74784644151450663,11302.270232977309,23045.880369033504,8002.0417948033,0.37418297049037524,5.6127445573556284E-2,1.5884067097316428,422.91159329026834,1.2418777687180409,4978.8620462904764,0.24943004187941048]
[105.11531995000594,32.039149520761811,86,0.6,143.33333333333334,14,7.5082371392861385,15,21600,424.5,2.4700194365382858E-4,2.629639302124301E-4,9.8600873320584433E-3,3.6827426185238286E-2,0.35873181170648821,24870.452559897534,47916.332928931035,16637.615600323275,0.1974395547113616,2.9615933206704241E-2,0.83813090974973004,423.66186909025026,0.75027579998192095,6024.4230760114842,0.12453902896850445]
[115.62685194500655,35.243064472838,86,0.6,143.33333333333334,14,8.2590608532147538,15,21600,424.5,1.1130442493543022E-4,1.178597165083696E-4,4.4431688839096069E-3,1.659523578140238E-2,0.16078261986769612,58272.129330210679,106188.46225914171,36870.993839979761,9.7341057078526402E-2,1.460115856177896E-2,0.41321278729834454,424.08678721270167,0.42491812245140181,7289.5519219739072,5.8291391158146799E-2]
[127.18953713950721,38.767370920121799,86,0.6,143.33333333333334,14,9.0849669385362297,15,21600,424.5,4.6523058854179839E-5,4.9019707017052196E-5,1.8571571400247872E-3,6.9364819179925799E-3,6.6872016604493087E-2,146276.54361096208,252465.00587010378,87661.460371563808,4.4534241758665161E-2,6.6801362637997743E-3,0.18904785626553361,424.31095214373448,0.22416493103281709,8820.3578255884058,2.5414493999608576E-2]
[139.90849085345795,42.644108012133984,86,0.6,143.33333333333334,14,9.9934636323898527,15,21600,424.5,1.7902377794190038E-5,1.8777625857105222E-5,7.146462327017461E-4,2.6692036791410214E-3,2.5616181420106958E-2,396056.87513162615,648521.88100172998,225181.20868115625,1.8765352110560438E-2,2.8148028165840655E-3,7.9658919709329049E-2,424.42034108029065,0.10938893655617221,10672.632968961989,1.0249479849470668E-2]
[153.89933993880376,46.908518813347392,86,0.6,143.33333333333334,14,10.992809995628841,15,21600,424.5,6.2900826357608422E-6,6.5701968734215965E-6,2.5109423511819774E-4,9.378369681664686E-4,8.962973080630595E-3,1165258.258843099,1813780.139844829,629784.7707794545,7.2224925863398279E-3,1.0833738879509741E-3,3.0659481029012569E-2,424.46934051897097,4.8999438680311869E-2,12913.885892444006,3.7943217934875619E-3]
[169.28927393268415,51.599370694682129,86,0.6,143.33333333333334,14,12.092090995191725,15,21600,424.5,1.999690623669107E-6,2.0807927119453955E-6,7.9825785557822231E-5,2.9814930905846604E-4,2.8385890747024763E-3,3755690.0789058809,5569470.2187507097,1933843.8259551076,2.5161134814975488E-3,3.774170222246323E-4,1.0680901728957094E-2,424.48931909827104,1.9978579300072852E-2,15625.801929857247,1.2785634548392981E-3]
[186.21820132595258,56.75930776415035,86,0.6,143.33333333333334,14,13.301300094710898,15,21600,424.5,5.6949901905970677E-7,5.905314441158375E-7,2.2733869946060587E-5,8.4911004248536297E-5,8.0559495230463952E-4,13378937.652787713,18948407.871538423,6579308.288728619,7.8548359535477526E-4,1.1782253930321629E-4,3.3343778622810208E-3,424.4966656221377,7.3465238666585719E-3,18907.220335127276,3.8855652689515866E-4]
[204.84002145854785,62.435238540565386,86,0.6,143.33333333333334,14,14.631430104181989,15,21600,424.5,1.4370620950703018E-7,1.4853835849785887E-7,5.7366179186195312E-6,2.1426267926043948E-5,2.0263400538925313E-4,53193118.063721783,72141525.935260206,25049140.949743129,2.1733286101513488E-4,3.2599929152270231E-5,9.2257799500924758E-4,424.49907742200497,2.4117998672750218E-3,22877.736605503989,1.0542126211448664E-4]
[225.32402360440267,68.678762394621941,86,0.6,143.33333333333334,14,16.094573114600191,15,21600,424.5,3.174399196608226E-8,3.2715710067473222E-8,1.2671905671009531E-6,4.7329567681220593E-6,4.4630326046192111E-5,238586478.84061578,310728004.77587599,107891668.32495694,5.2654538767700939E-5,7.8981808151551404E-6,2.2351851706889047E-4,424.49977648148291,6.9905947793813539E-4,27682.061292659899,2.5253158373848992E-5]
[247.85642596484297,75.546638634084147,86,0.6,143.33333333333334,14,17.704030426060211,15,21600,424.5,6.0572671893799522E-9,6.2260464442837391E-9,2.4180045953242753E-7,9.0312471635361673E-7,8.4934877529491289E-6,1221548570.3535292,1532276575.1294053,532040477.47548795,1.1022611568366331E-5,1.6533917352549496E-6,4.6790986107715074E-5,424.49995320901388,1.7672753097031091E-4,33495.294164118444,5.2761898463823255E-6]
[272.64206856132728,83.101302497492554,86,0.6,143.33333333333334,14,19.474433468666234,15,21600,424.5,9.8394085791346639E-10,1.0088941783241094E-9,3.9278001804731579E-8,1.4670333674067244E-7,1.3763196957010979E-6,7232425865.3735876,8764702440.5029926,3043299458.5079832,1.9647642552697553E-6,2.9471463829046328E-7,8.3404242636201105E-6,424.49999165957576,3.8450561874014966E-5,40529.305938583275,9.4871009960747002E-7]
[299.90627541746005,91.411432747241832,86,0.6,143.33333333333334,14,21.421876815532862,15,21600,424.5,1.3389076443515751E-10,1.3698094605256194E-10,5.3447945014430041E-9,1.9962807462889618E-8,1.8686754075742623E-7,50231292780.738983,58995995221.241974,20484720562.93124,2.9343889524131341E-7,4.4015834286197009E-8,1.2456481102993753E-6,424.49999875435191,7.0947761514617014E-6,49040.460185685894,1.4467189183376689E-7]
[329.8969029592061,100.55257602196602,86,0.6,143.33333333333334,14,23.56406449708615,15,21600,424.5,1.4994595836480069E-11,1.5309517522096042E-11,5.9857028762421939E-10,2.2356600242764595E-9,2.0885035269350931E-8,415749392725.20032,474745387946.44226,164842148592.51468,3.607544583099417E-8,5.411316874649125E-9,1.5314026755257025E-7,424.49999984685974,1.0925078299806046E-6,59338.956824679859,1.841130832832936E-8]
[362.88659325512674,110.60783362416264,86,0.6,143.33333333333334,14,25.920470946794769,15,21600,424.5,1.3553939919250304E-12,1.3812958730021212E-12,5.4106064640762864E-11,2.0208615143324929E-10,1.8843450150157651E-9,4172722615445.3086,4647468003391.751,1613704167844.3579,3.5803839545078994E-9,5.3705759317618498E-10,1.5198729886886035E-8,424.49999998480126,1.3794152664559078E-7,71800.137757862685,1.921187492853871E-9]
[399.17525258063944,121.66861698657891,86,0.6,143.33333333333334,14,28.512518041474245,15,21600,424.5,9.6792393027082796E-14,9.8475343663310587E-14,3.863862098443726E-12,1.4431524937687315E-11,1.3433872247125627E-10,51772021994677.859,56419489998069.609,19590100693774.168,2.8077800128405198E-10,4.2116700192607798E-11,1.1919026154508008E-9,424.49999999880811,1.4006843684910564E-8,86878.166687013698,1.6122397857877757E-10]
[439.0927778387034,133.83547868523681,86,0.6,143.33333333333334,14,31.363769845621672,15,21600,424.5,5.3337117168027871E-15,5.4180827312641308E-15,2.1291679957549063E-13,7.9524424641445748E-13,7.3912746610985397E-12,811137197976983.62,867556687975053.25,301234961102449.06,1.6993149978790546E-11,2.5489724968185818E-12,7.2135921659965871E-11,424.49999999992787,1.1197585081390571E-9,105122.58169128676,1.0651931203777408E-11]
[{"$f":"A488*1.1","v":483.00205562257378},147.2190265537605,86,0.6,143.33333333333334,14,34.500146830183844,15,21600,424.5,2.2099108687683562E-16,2.2417120888098476E-16,8.8217581771986156E-15,3.2949266791836824E-14,3.0581130967028721E-13,1.6429428032608466E+16,1.729698472058352E+16,6005897472424833,7.7339396214937868E-13,1.160090943224068E-13,3.2830573693241125E-12,424.4999999999967,6.8837380240438506E-11,127198.32384645683,5.4118150427464149E-13]
[{"$f":"A489*1.1","v":531.3022611848312},161.94092920913656,86,0.6,143.33333333333334,14,37.950161513202225,15,21600,424.5,6.691066224680076E-18,6.7786540406675925E-18,2.6710112618544779E-16,9.9762270630264753E-16,9.2473475087468356E-15,4.4151966260763405E+17,4.588166473282176E+17,1.5931133587785334E+17,{"$f":"G490*BESSELK(G490,1)*100","v":2.5725101568545604E-14},3.8587652352818405E-15,1.0920305615847609E-13,424.49999999999989,3.1832314562052488E-12,153909.97185421293,2.0682425042741732E-14]